## United Utilities 2023
EDM STORM OVERFLOW REGULATORY ANNUAL RETURN 2023 | [19 empty] | Complete columns U & V when data in column T is <90% |  | Enter in columns W, X, Y when relevant spill frequency data (column Q + valid historic) is above the SOAF threshold (pg. 2 of SOAF)
Water Company Name | Site Name (EA Consents Database) | Site Name (WaSC operational) [optional] | EA Permit Reference (EA Consents Database) | WaSC Supplementary Permit Ref. [optional] | Activity Reference on Permit | Storm Discharge Asset Type | Outlet Discharge NGR (EA Consents Database) | WFD Waterbody ID (Cycle 2) (discharge outlet) | WFD Waterbody Catchment Name (Cycle 2) (discharge outlet) | Receiving Water / Environment (common name) (EA Consents Database) | Shellfish Water (only populate for storm overflow with a Shellfish Water EDM requirement) | Bathing Water (only populate for storm overflow with a Bathing Water EDM requirement) | Treatment Method (over & above Storm Tank settlement / screening) | Initial EDM Commission Date | Total Duration (hrs) all spills prior to processing through 12-24h count method | Counted spills using 12-24h count method | Long-term average spill count | No. full years EDM data (years) | EDM Operation - % of reporting period EDM operational | EDM Operation - Reporting % - Primary Reason <90% | EDM Operation - Action taken / planned - Status & timeframe | High Spill Frequency - Operational Review - Primary Reason | High Spill Frequency - Action taken / planned - Status & timeframe | High Spill Frequency - Environmental Enhancement - Planning Position (Hydraulic capacity) | Unique ID
United Utilities | WRENBURY WWTW | WRENBURY WWTW | 16810119 | 16810119 | SO | Inlet SO at WwTW | SJ6077747560 | GB112068055470 | Weaver (Marbury Brook to Barnett Brook) | River Weaver | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 37.25 | 14 | 26.2 | 5 (installed 2018) | 100 | [5 empty] | UUG0001
United Utilities | BADDILEY LANE SPS | Ravensmoor PS | 016810297 | CRE0023 | SO | Storm discharge at pumping station | SJ6185050450 | GB112068055250 | Edleston Brook | TRIB RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 786.21 | 60 | 45 | 3 (installed 2020) | 80.67 | Comms failure / issue | Resolved - Nov | Data collection - EDM non-representative location | Resolved - Dec | Other investigation - non-WINEP/Green Recovery | UUG0002
United Utilities | WHITCHURCH ROAD SPS | Newhall PS | 016810293 | CRE0025 | SO | Storm discharge at pumping station | SJ6097045530 | GB112068055210 | Sales Brook | SALES BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 21.96 | 15 | 13 | 4 (installed 2019) | 99.92 | [5 empty] | UUG0003
United Utilities | BROOMHALL SPS | Sandford Banks PS | 016810292 | CRE0024 | SO | Storm discharge at pumping station | SJ6220047200 | GB112068055470 | Weaver (Marbury Brook to Barnett Brook) | TRIB RIVER WEAVER | N/A | N/A | Not Applicable | Dec 2023 | 1.12 | 1 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0004
United Utilities | WRENBURY HALL ROAD SPS | Wrenbury Hall Road PS | 016810369 | CRE0028 | SO | Storm discharge at pumping station | SJ6010048400 | GB112068055470 | tockport | SHROPSHIRE UNION CANAL | N/A | N/A | Not Applicable | Dec 2023 | 8.79 | 7 |  | <1 yr (installed 2023) | 42.2222 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0005
United Utilities | WREAY WWTW WREAY | WREAY WwTW | 017680463 | 17680463 | SO | Inlet SO at WwTW | NY4366248788 | GB102076074030 | Petteril d/s Blackrack Beck | THE RIVER PETTERIL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 219.51 | 88 | 17.6 | 5 (installed 2018) | 99.97 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0006
United Utilities | WRAY WASTEWATER TREATMENT WORKS | Wray Wastewater Treatment Works (WRAYZ) (017270020) | 017270020 | 17270020 | SO | Inlet SO at WwTW | SD6011068120 | GB112072066050 | Hindburn | RIVER HINDBURN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 165.79 | 181 | 221.4 | 5 (installed 2018) | 100 |  |  | Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | Resolved - Dec | Other investigation - non-WINEP/Green Recovery | UUG0007
United Utilities | Hindburn Bridge PS | Hindburn Bridge PS | 1456 / 01LAN0047 | LAN0047 | SO | Storm discharge at pumping station | SD6056067502 | GB112072066020 | Roeburn | River Roeburn | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.12 | 1 | 0.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0008
United Utilities | WORSLEY STW | WORSLEY WwTW | 016940139 | 16940139 | SO | Inlet SO at WwTW | SD7215002750 | GB112069061100 | Astley Brook (Mersey) | LITTLE HULTON STREAM | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 502.49 | 113 | 88.75 | 4 (installed 2019) | 97.81 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0009
United Utilities | WORSLEY STW | WORSLEY WwTW | 016940139 | 16940139 | SO | Inlet SO at WwTW | SD7215002750 | GB112069061100 | Astley Brook (Mersey) | LITTLE HULTON STREAM | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2.02 | 7 | 11.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0010
United Utilities | WORSLEY STW | WORSLEY WwTW | 016940139 | 16940139 | ST | Storm tank at WwTW | SD7215002750 | GB112069061100 | Astley Brook (Mersey) | LITTLE HULTON STREAM | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 822.62 | 102 | 74.75 | 4 (installed 2019) | 99.69 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0011
United Utilities | BEECH GROVE CSO | Beech Grove CSO | 01SAL0059 | SAL0059 | SO | SO on sewer network | SD7144004040 | GB112069061100 | Astley Brook (Mersey) | TRIB HONKSFORD BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.1 | 1 | 4.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0012
United Utilities | TYNESBANK | Tynesbank CSO | 01SAL0062 | SAL0062 | SO | SO on sewer network | SD7338002780 | GB112069061090 | Shaw Brook | ELLEN BROOK CULVERT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 118.41 | 57 | 58.75 | 4 (installed 2019) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0013
United Utilities | LITTLE HULTON CSO | LITTLE HULTON CSO | 01SAL0130 | SAL0130 | SO | SO on sewer network | SD7135003630 | GB112069061100 | Astley Brook (Mersey) | ASTLEY BROOK | N/A | N/A | Not Applicable | Dec 2023 | 141.17 | 58 |  | <1 yr (installed 2023) | 95.9677 | [5 empty] | UUG0014
United Utilities | CSO SOUTH OF ASHAWE GROVE | South of Ashawe Grove CSO | 016982741 | SAL0150 | SO | SO on sewer network | SD7156003030 | GB112069061100 | Astley Brook (Mersey) | TRIB OF HONKSFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 123.47 | 54 | 44.75 | 4 (installed 2019) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0015
United Utilities | CSO SOUTH OF ASHAWE GROVE | South of Ashawe Grove CSO | 016982742 | SAL0151 | SO | SO on sewer network | SD7156003030 | GB112069061100 | Astley Brook (Mersey) | TRIBUTARY OF HONKSFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.8 | 1 | 1.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0016
United Utilities | ALLERBY WWTW ALLER | ALLERBY WwTW | 017570082 | 17570082 | ST | Storm tank at WwTW | NY0892039130 | 357 |  | BRUNSOW BECK | N/A | Allonby South | Not Applicable | Commissioned in 2016 - full year data expected | 315.35 | 51 | 52.1429 | 7 (installed 2016) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0017
United Utilities | HIGH STREET WORKINGTON CSO | High Street (Workington) Combined Sewer Overflow (Site ID 02633) (ALL0006) | 017580412 | ALL0006 | SO | SO on sewer network | NY0096028430 | GB112075070520 | Derwent - conf Cocker to tidal | STAN BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 87.51 | 83 | 94 | 4 (installed 2019) | 99.83 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0018
United Utilities | HAWTHORN AVENUE/RAILWAY BRIDGE CSO | Hawthorn Avenue/Railway Bridge CSO | 017570201 | ALL0032 | SO | SO on sewer network | NY0431036400 | GB112075073640 | Ellen (lower) | GILL BECK | N/A | Allonby South | Not Applicable | Commissioned in 2016 - full year data expected | 0 | 0 | 1.4286 | 7 (installed 2016) | 96.52 | [5 empty] | UUG0019
United Utilities | ALLONBY WWTW ALLON | ALLONBY WwTW | 017580272 | 17580272 | SO | Inlet SO at WwTW | NY0812244142 | 357 |  | IRISH SEA (ALLONBY BAY) | 118 Sillloth | Allonby Allonby South | Not Applicable | Commissioned in 2017 - full year data expected | 47.23 | 4 | 5.6667 | 6 (installed 2017) | 100 | [5 empty] | UUG0020
United Utilities | ASKAM-IN-FURNESS WWTW ASKAM | ASKAM-IN-FURNESS WwTW | 017470136 | 17470136 | SO | Inlet SO at WwTW | SD2118078600 | 344 |  | BLEA BECK | N/A | Haverigg; Walney Biggar Bank; Walney West Shore; Walney Sandy Gap | Not Applicable | Commissioned in 2018 - full year data expected | 1.84 | 6 | 5.8 | 5 (installed 2018) | 100 | [5 empty] | UUG0021
United Utilities | NORTHSIDE CSO 021QB | Northside Sewerage System | 017570206 | ALL0090 | SO | SO on sewer network | NY0117029340 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 133.83 | 61 | 60.4 | 5 (installed 2018) | 96.35 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0022
United Utilities | ASKAM-IN-FURNESS WWTW ASKAM | ASKAM-IN-FURNESS WwTW | 017470136 | 17470136 | ST | Storm tank at WwTW | SD2118078600 | 344 |  | BLEA BECK | N/A | Haverigg; Walney Biggar Bank; Walney West Shore; Walney Sandy Gap | Not Applicable | Commissioned in 2018 - full year data expected | 3659.57 | 167 | 175.6 | 5 (installed 2018) | 100 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0023
United Utilities | K SHOES CSO 042B6 | K. Shoes, CSO | 01BRW0056 | BRW0056 | SO | SO on sewer network | SD2144077990 | 344 |  | BLEA BECK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 1.03 | 5 | 14.5 | 6 (installed 2017) | 99.99 | [5 empty] | UUG0024
United Utilities | WINSFORD WASTEWATER TREATMENT WORKS | WINSFORD WwTW | 016810116 | 16810116 | SO | Inlet SO at WwTW | SJ6544067440 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 29.59 | 16 | 35.1429 | 7 (installed 2016) | 99.85 | [5 empty] | UUG0025
United Utilities | WINSFORD WASTEWATER TREATMENT WORKS | WINSFORD WwTW | 016810116 | 16810116 | ST | Storm tank at WwTW | SJ6544067440 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 410.69 | 64 | 54 | 7 (installed 2016) | 96.75 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0026
United Utilities | OFF JOHN ST CSO (472JC) | Off John Street CSO | 01VRY0004 | VRY0004 | SO | SO on sewer network | SJ6552066270 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER VIA CULVERT | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 4.33 | 5 | 2 | 3 (installed 2020) | 99.99 | [5 empty] | UUG0027
United Utilities | DEAN STREET CSO (471RJ) | Dean Street CSO | 01VRY0006 | VRY0006 | SO | SO on sewer network | SJ6553066360 | GB112068060460 | Weaver (Marbury Brook to Dane) | CULVERT TRIB DENE BROOK VIASWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.93 | 4 | 1.6667 | 3 (installed 2020) | 99.99 | [5 empty] | UUG0028
United Utilities | RILSHAW LANE | Rilshaw Lane PS | 016881540 | VRY0044 | SO | Storm discharge at pumping station | SJ6703065880 | GB112068060460 | Weaver (Marbury Brook to Dane) | DITCH COURSE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 96.59 | 52 | 71 | 3 (installed 2020) | 99.99 |  |  | Data collection - EDM non-representative location | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0029
United Utilities | CHURCH ST | Church Street PS | 016892145 | VRY0045 | SO | Storm discharge at pumping station | SJ6550066450 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | Not Applicable | Dec 2023 | 19.14 | 3 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0030
United Utilities | WINSFORD HILL STREET | Hill Street PS | 016892221 | VRY0090 | SO | Storm discharge at pumping station | SJ6555066270 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 69.51 | 23 | 28.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG0031
United Utilities | O/S 90 QUEENSWAY CSO | Outside of 90 Queensway CSO | 01VRY0097 | VRY0097 | SO | SO on sewer network | SJ6553066260 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 9.7 | 20 | 17 | 3 (installed 2020) | 100 | [5 empty] | UUG0032
United Utilities | MEADOWBANK/BRADFORD RD PS | Meadowbank/Bradford Road PS | 016881775 | VRY0142 | SO | Storm discharge at pumping station | SJ6530068270 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 707.33 | 83 | 65.6667 | 3 (installed 2020) | 99.87 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0033
United Utilities | GLEBE ROAD PUMPING STATION | Glebe Road PS | 17370148 | LAK0045 | SO | Storm discharge at pumping station | SD3951796246 | GB31247007 | Windermere (N Basin) | WINDERMERE | N/A | Windermere, Rayrigg Meadow | Not Applicable | Commissioned in 2017 - full year data expected | 241.9 | 41 | 77.3333 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0034
United Utilities | WILPSHIRE WWTW (WILPS) | WILPSHIRE WwTW | 017160049 | 17160049 | ST | Storm tank at WwTW | SD6755032440 | GB112071065710 | Showley Brook | SHOWLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 747.91 | 111 | 112.75 | 4 (installed 2019) | 99.93 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0035
United Utilities | WILMSLOW STW | WILMSLOW WwTW | 016910014 | 16910014 | SO | Inlet SO at WwTW | SJ8413082320 | GB112069061360 | Dean (Bollington to Bollin) | RIVER DEAN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 281.33 | 77 | 80 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0036
United Utilities | WILMSLOW STW | WILMSLOW WwTW | 016910014 | 16910014 | ST | Storm tank at WwTW | SJ8413082320 | GB112069061360 | Dean (Bollington to Bollin) | RIVER DEAN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1809.54 | 149 | 172.6 | 5 (installed 2018) | 98.74 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0037
United Utilities | QUARRY BANK MILL CSO 272M4 | QUARRY BANK MILL CSO | 01MAC0043 | MAC0043 | SO | SO on sewer network | SJ8344082800 | GB112069061381 | Bollin (River Dean to Ashley Mill) | TRIBUTARY OF RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 23.33 | 14 | 19.6 | 5 (installed 2018) | 100 | [5 empty] | UUG0038
United Utilities | THE CARRS COMBINED SEWER OVERFLOW | THE CARRS CSO | 01MAC0044 | MAC0044 | SO | SO on sewer network | SJ8420081700 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 32.1 | 14 | 47 | 5 (installed 2018) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0039
United Utilities | CHANCEL LANE CSO 271I4 | CHANCEL LANE CSO | 01MAC0046 | MAC0046 | SO | SO on sewer network | SJ8481081550 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 338.4 | 71 | 63.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0040
United Utilities | OPP RIVER ST CSO (273BY) | Opp River Street CSO | 01MAC0045 | MAC0045 | SO | SO on sewer network | SJ8476081560 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | Not Applicable | Dec 2023 | 264.13 | 71 |  | <1 yr (installed 2023) | 98.6957 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0041
United Utilities | REAR OF KNOWLE HOUSE | Rear of Knowle House CSO | 01MAC0048 | MAC0048 | SO | SO on sewer network | SJ8519083240 | GB112069061360 | Dean (Bollington to Bollin) | TRIB RIVER DEAN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 121.7 | 63 | 46.25 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0042
United Utilities | WILMSLOW PARK SOUTH CSO | Wilmslow Park South Combined Sewer Overflow (Site ID 272YI) (MAC0047) | 01MAC0047 | MAC0047 | SO | SO on sewer network | SJ8529081251 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0043
United Utilities | REEMAN COURT MANHOLE H4 CSO 272NY | Reeman Court (Manhole H4) | EPRJB3298WZ | MAC0066 | SO | SO on sewer network | SJ8449382562 | GB112069061360 | Dean (Bollington to Bollin) | RIVER DEAN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 46.83 | 23 | 55.6 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0044
United Utilities | DEAN ROAD CSO 278A2 | Dean Road CSO | EPRJB3299AW | MAC0067 | SO | SO on sewer network | SJ8630082781 | GB112069061360 | Dean (Bollington to Bollin) | RIVER DEAN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.13 | 2 | 5.2 | 5 (installed 2018) | 100 | [5 empty] | UUG0045
United Utilities | HAWTHORN LANE CSO | Hawthorn Lane | 016982619 | MAC0155 | SO | SO on sewer network | SJ8469081460 | GB112069061320 | Bollin (Source to Dean) | CLVRT'D TRIB OF RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 3.6 | 9 | 10.5 | 4 (installed 2019) | 93.17 | [5 empty] | UUG0046
United Utilities | BOLLIN WALK CSO 27074 | The Wilmslow Park Road CSO | 016993490 | MAC0165 | SO | SO on sewer network | SJ8529081230 | GB112069061320 | Bollin (Source to Dean) | WHITFIELD BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 26.43 | 27 | 28.4 | 5 (installed 2018) | 99.97 | [5 empty] | UUG0047
United Utilities | WIGTON WASTEWATER TREATMENT WORKS | WIGTON WwTW | 017570019 | 17570019 | ST | Storm tank at WwTW | NY2737051370 | GB102075073460 | Pow Beck (Wampool) | RIVER WAMPOOL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 645.81 | 76 | 66.25 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0048
United Utilities | MEETING HOUSE LANE CSO | Meeting House Lane CSO | 017580314 | ALL0009 | SO | SO on sewer network | NY2535048600 | GB102075073390 | Wiza Beck | WIZA BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 90.7 | 48 | 43 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0049
United Utilities | STAMPERY WWN PUMPING STATION | Stampery PS | 017570092 | ALL0075 | SO | Storm discharge at pumping station | NY2574049030 | GB102075073390 | Wiza Beck | SPEET GILL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 281.46 | 51 | 55.25 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0050
United Utilities | STATION HILL CSO | Station Hill CSO | 017580225 | ALL0091 | SO | SO on sewer network | NY2539048820 | GB102075073390 | Wiza Beck | WIZA BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 18.9 | 19 | 22 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0051
United Utilities | GEORGE STREET CSO | George Street CSO | 017580254 | ALL0099 | SO | SO on sewer network | NY2513048150 | GB102075073390 | Wiza Beck | WIZA BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 59.8 | 51 | 74.4 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0052
United Utilities | WIGAN WASTEWATER TREATMENT WORKS | WIGAN (HOSCAR) WwTW | 017081316 | 17081316 | ST | Storm tank at WwTW | SD4817012020 | GB112070064820 | Douglas - Lower | RIVER DOUGLAS | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 1192.05 | 77 | 52 | 6 (installed 2017) | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0053
United Utilities | NR HARRISONS FARM | Near Harrison's Farm CSO | 01CHR0021 | CHR0021 | SO | SO on sewer network | SD5987012400 | GB112070064850 | Douglas - Upper | RIVER DOUGLAS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 586.28 | 69 | 23 | 3 (installed 2020) | 95.37 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0054
United Utilities | Grimeford Lane PS | Grimeford Lane PS | 01CHR0057 | CHR0057 | SO | Storm discharge at pumping station | SD6151412650 | GB112070064850 | Douglas - Upper | Unnamed tributary of River Douglas | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 25.99 | 13 | 20 | 5 (installed 2018) | 100 | [5 empty] | UUG0055
United Utilities | HARRISON ROAD WAGON AND HORSE CSO | Harrisons Road Wagon & Horses CSO | 017091496 | CHR0061 | SO | SO on sewer network | SD6017012550 | GB112070064850 | Douglas - Upper | River Douglas | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 79.25 | 44 | 60.4 | 5 (installed 2018) | 94.6 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0056
United Utilities | GATHURST LANE SHEVINGTON CSO | Gathurst Lane (Shevington) CSO | 017091492 | WIG0001 | SO | SO on sewer network | SD5401007370 | GB112071065510 | Mearley Brook | TRIB OF PENDLETON BROOK BY SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 72 | 56 | 67.75 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0057
United Utilities | WIGAN ROAD CSO 50087 | Wigan Road Shevington CSO | 017091497 | WIG0002 | SO | SO on sewer network | SD5505008310 | GB112070064820 | Douglas - Lower | MILL BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 238.94 | 91 | 85.2 | 5 (installed 2018) | 94.88 |  |  | not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0058
United Utilities | SPRINGFIELD ROAD CSO | Springfield Road CSO | 01WIG0004 | WIG0004 | SO | SO on sewer network | SD5624006711 | GB112070064820 | Douglas - Lower | RIVER DOUGLAS VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 9 | 27 | 25.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0059
United Utilities | LYNTON AVENUE CSO | Lynton Avenue CSO | 01WIG0005 | WIG0005 | SO | SO on sewer network | SD5624006710 | GB112070064820 | Douglas - Lower | CULVERTED TRIB. RIVER DOUGLAS | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0060
United Utilities | ORMSKIRK ROAD/FRANCE STREET CSO | ORMSKIRK ROAD / FRANCE STREET CSO | 01WIG0008 | WIG0008 | SO | SO on sewer network | SD5710005181 | GB112070064820 | Douglas - Lower | RIVER DOUGLAS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0.66667 | 3 (installed 2020) | 98.25 | [5 empty] | UUG0061
United Utilities | CHESTNUT ROAD CSO | Chestnut Road CSO | 01WIG0013 | WIG0013 | SO | SO on sewer network | SD5877006571 | GB112070064780 | Douglas - Mid | RIVER DOUGLAS VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 8.8 | 23 | 18.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG0062
United Utilities | BRADSHAW STREET CSO | Bradshaw Street CSO | 017091489 | WIG0014 | SO | SO on sewer network | SD5877006570 | GB112070064780 | Douglas - Mid | RIVER DOUGLAS VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 31.7 | 44 | 33.3333 | 3 (installed 2020) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0063
United Utilities | HOLLY STREET/NEW SPRINGS CSO | HOLLY STREET / NEW SPRINGS CSO | 01WIG0015 | WIG0015 | SO | SO on sewer network | SD5984007060 | GB112070064780 | Douglas - Mid | YELLOW BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 68.93 | 31 | 25.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0064
United Utilities | PLATT LANE CSO | PLATT LANE CSO | WIG0016 | WIG0016 | SO | SO on sewer network | SD5951306053 | GB112069061060 | Platt Brook (Source to Fallowfield Bk) | Clarington Brook | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.37 | 5 | 6 | 4 (installed 2019) | 100 | [5 empty] | UUG0065
United Utilities | WESTMOORLAND STREET/SCHOLES CSO | WESTMOORLAND STREET / SCHOLES CSO | 01WIG0017 | WIG0017 | SO | SO on sewer network | SD5952006050 | GB112070064780 | Douglas - Mid | CLARINGTON BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0066
United Utilities | ST MARY'S ROAD CSO | ST MARYS ROAD CSO | 01WIG0018 | WIG0018 | SO | SO on sewer network | SD6092007880 | GB112070061610 | Poolstock Brook | TRIB. OF INCE BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1052.97 | 161 | 144.5 | 4 (installed 2019) | 99.6 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0067
United Utilities | ARBOUR LANE PUMPING STATION | Arbour Lane Pumping Station (50033) (WIG0029 ) | 017091563 | WIG0029 | SO | Storm discharge at pumping station | SD5503009730 | GB112070064820 | Douglas - Lower | MILL BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 69.75 | 29 | 26.6 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0068
United Utilities | GATHURST LANE SHEVINGTON CSO | Gathurst PS | 017091564 | WIG0031 | SO | Storm discharge at pumping station | SD5401007370 | GB112070064820 | Douglas - Lower | RIVER DOUGLAS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 94.51 | 55 | 47.8 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0069
United Utilities | BORSDANE BROOK (HINDLEY) CSO | Borsdane Brook (Hindley) CSO | 016983226 | WIG0049 | SO | SO on sewer network | SD6085002400 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 258.1 | 59 | 64 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0070
United Utilities | HM BORSTAL CSO | Adjacent HM Borstal Hindley CSO | 016983227 | WIG0050 | SO | SO on sewer network | SD6175002350 | GB112069064520 | Hey/Borsdane Brook | BROOKSIDE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 1 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0071
United Utilities | LORD STREET | Lord Street CSO | 016993630 | WIG0053 | SO | SO on sewer network | SD6142003680 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0072
United Utilities | 42 BRIDGE STREET CSO | 42 Bridge Street CSO | 01WIG0054 | WIG0054 | SO | SO on sewer network | SD6205004610 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0073
United Utilities | CHAPEL GREEN ROAD/ROMFORD ST CSO | Chapel Green Road/Romford Street CSO | 016993521 | WIG0057 | SO | SO on sewer network | SD6196004412 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 11.07 | 14 | 42.75 | 4 (installed 2019) | 97.32 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0074
United Utilities | CHAPEL GREEN ROAD | Junction of Romford Street & Chapel Green Road CSO | 01WIG0058 | WIG0058 | SO | SO on sewer network | SD6196004410 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0075
United Utilities | CHAPELGREEN/ARUNDEL ST | Chapel Green Road/ Arundle Street CSO | 01WIG0059 | WIG0059 | SO | SO on sewer network | SD6196004411 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0076
United Utilities | CHAPEL GREEN ROAD/BRIDGEWATER ST | Chapel Green Road/Bridgewater Street CSO | 01WIG0060 | WIG0060 | SO | SO on sewer network | SD6199004420 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0077
United Utilities | TEMPLETON ROAD WW NETWORK PS | Templeton Road PS | 01WIG0095 | WIG0095 | SO | Storm discharge at pumping station | SD6050002450 | GB112069064520 | Hey/Borsdane Brook | HEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 25.72 | 65 | 9.2857 | 7 (installed 2016) | 99.99 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0078
United Utilities | STRANGEWAY NO.2 WW NTWK PS | Strangeways PS No2 | 01WIG0096 | WIG0096 | SO | Storm discharge at pumping station | SD6105003340 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0079
United Utilities | STRANGEWAY NO.1 WW NTWK PS | Strangeways No1 Ww Ntwk PS | 01WIG0097 | WIG0097 | SO | Storm discharge at pumping station | SD6132003450 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | Not Applicable | Dec 2023 | 3643.59 | 174 |  | <1 yr (installed 2023) | 100 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0080
United Utilities | BAMFURLONG PUMPING STATION | Bamfurlong Pumping Station (50013) (WIG0127) | 01WIG0127 | WIG0127 | SO | Storm discharge at pumping station | SD6012001780 | GB112069064520 | Hey/Borsdane Brook | HEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 62.42 | 26 | 37.4 | 5 (installed 2018) | 100 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG0081
United Utilities | BICKERSHAW LANE PUMPING STATION | Bickershaw Lane PS | 01WIG0128 | WIG0128 | SO | Storm discharge at pumping station | SD6085002380 | GB112069064520 | Hey/Borsdane Brook | HEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 380.83 | 55 | 49.25 | 4 (installed 2019) | 99.88 |  |  | Performance - Pump failure / issue | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0082
United Utilities | CRANKWOOD ROAD PUMPING STATION | Crankwood Road PS | 016993851 | WIG0129 | SO | Storm discharge at pumping station | SD6175000190 | GB112069064520 | Hey/Borsdane Brook | TRIBUTARY OF HEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.4 | 1 | 5.4 | 5 (installed 2018) | 99.59 | [5 empty] | UUG0083
United Utilities | ABRAM HALL PUMPING STATION | Abram Hall PS | 01WIG0130 | WIG0130 | SO | Storm discharge at pumping station | SD6058001410 | GB112069064520 | Hey/Borsdane Brook | HEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 156.85 | 24 | 36 | 7 (installed 2016) | 98.41 | [5 empty] | UUG0084
United Utilities | OLD FOLD ROAD CSO | Old Fold Road CSO | 016983225 | WIG0132 | SO | SO on sewer network | SD6188008070 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 3.63 | 5 | 7 | 4 (installed 2019) | 100 | [5 empty] | UUG0085
United Utilities | SWAN LANE HINDLEY CSO 503J8 | Swan Lane Hindley CSO | 016920473 | WIG0150 | SO | SO on sewer network | SD6424003810 | GB112069060820 | Westleigh Brook | MARSH BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 45.83 | 46 | 38.6 | 5 (installed 2018) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0086
United Utilities | STRANGEWAYS CSO 50083 | Strangeways CSO | 016940235 | WIG0153 | SO | SO on sewer network | SD6142003740 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 116.46 | 36 | 31.8 | 5 (installed 2018) | 82.55 | Sensor failure / issue | N/A - Ongoing investigation |  |  |  | UUG0087
United Utilities | WINSTANLEY ROAD PUMPING STATION | Winstanley Road PS | 017020090 | WIG0155 | SO | Storm discharge at pumping station | SD5327003840 | GB112070061600 | Smithy Brook | SMITHY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.27 | 2 | 1.2 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0088
United Utilities | MILL LANE CSO 49201 | Mill Lane CSO | 017091498 | WIG0164 | SO | SO on sewer network | SD5237109191 | GB112068055360 | Douglas - Lower | River Douglas | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1131.58 | 151 | 125.6667 | 3 (installed 2020) | 91.06 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0089
United Utilities | SOUTH OF BALL STREET CSO | WIG0165A South of Ball Street CSO | NPSWQD003177 | WIG0165A | SO | SO on sewer network | SD5635706786 | GB112070064820 | Douglas - Lower | RIVER DOUGLAS VIA SWS | N/A | N/A | Not Applicable | Dec 2023 | 0 | 0 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0090
United Utilities | NW JCT WOODHOUSE LANE | NW Junction Woodhouse Lane CSO | 017091491 | WIG0165 | SO | SO on sewer network | SD5622006750 | GB112070064820 | Douglas - Lower | THE RIVER DOUGLAS | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0091
United Utilities | Bradley Lane CSO | Bradley Lane CSO | 017091499 | WIG0166 | SO | SO on sewer network | SD5747311253 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | Bradley Brook (tributary of River Douglas) | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 340.88 | 103 | 92 | 3 (installed 2020) | 71.32 | Sensor failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0092
United Utilities | CHORLEY RD, M.H. E36 | Chorley Road M.H E36 Standish | 01LA1617 | WIG0167 | SO | SO on sewer network | SD5800009280 | GB112070064780 | Douglas - Mid | RIVER DOUGLAS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 186.9 | 75 | 59.3333 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0093
United Utilities | CLOSE BROOK CSO | Close Brook CSO | 017091500 | WIG0168 | SO | SO on sewer network | SD5636005900 | GB112070064820 | Douglas - Lower | CLOSE BROOK TRIB OF R DOUGLAS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 708.15 | 75 | 36 | 5 (installed 2018) | 95.11 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0094
United Utilities | LODGE RD, ORRELL(M.H. A4) | Lodge Road (Orrell) CSO | 01WIG0171 | WIG0171 | SO | SO on sewer network | SD5328000380 | GB112070061600 | Smithy Brook | Smithy Brook | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 397.81 | 112 | 99.8 | 5 (installed 2018) | 96.31 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0095
United Utilities | IRVINES FARM CSO | Irvine's Farm CSO | 017091502 | WIG0172 | SO | SO on sewer network | SD5403006540 | GB112070064820 | Douglas - Lower | ACKHURST BROOK TRIB R DOUGLAS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 413.23 | 108 | 102 | 5 (installed 2018) | 98.71 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0096
United Utilities | ORRELL HOUSE FARM CSO 50085 | Orrell House Farm CSO | 017091503 | WIG0173 | SO | SO on sewer network | SD5319006670 | GB112070064820 | Douglas - Lower | DEAN BROOK TRID OF R DOUGLAS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 461.71 | 109 | 99.2 | 5 (installed 2018) | 98.83 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0097
United Utilities | CENTRAL PARK CSO 50090 | Central Park CSO | 01WIG0174 | WIG0174 | SO | SO on sewer network | SD5875006330 | GB112070064780 | Douglas - Mid | RIVER DOUGLAS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 340 | 104 | 119.8 | 5 (installed 2018) | 92.26 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0098
United Utilities | DARBY LANE CSO | Wigan Road/Darby Lane CSO(502YD) (WIG0191) | 016982775 | WIG0191 | SO | SO on sewer network | SD6146004480 | GB112070064820 | Douglas - Lower | HOCKERY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 1.8 | 5 (installed 2018) | 100 | [5 empty] | UUG0099
United Utilities | DARBY LANE CSO | Darby Lane CSO | 016982776 | WIG0192 | SO | SO on sewer network | SD6146004480 | GB112069064520 | Hey/Borsdane Brook | HOCKERY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.47 | 7 | 21.25 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0100
United Utilities | CROSS STREET CSO | Cross Street CSO | 016982777 | WIG0193 | SO | SO on sewer network | SD6149004420 | GB112069064520 | Hey/Borsdane Brook | CULVRTD SECTION HOCKERY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.6 | 4 | 5.75 | 4 (installed 2019) | 96.41 | [5 empty] | UUG0101
United Utilities | GOWER STREET CSO 50126 | Gower Street CSO | 017081268 | WIG0202 | SO | SO on sewer network | SD5712005210 | GB112070064820 | Douglas - Lower | RIVER DOUGLAS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 169.37 | 68 | 55.4 | 5 (installed 2018) | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0102
United Utilities | BICKERSHAW LANE CSO 501D5 | Bickershaw Lane Opposite Pear Tree CSO | 016982784 | WIG0204 | SO | SO on sewer network | SD6161002240 | GB112069064520 | Hey/Borsdane Brook | TRIB BROOKSIDE BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 25.6 | 23 | 23.2 | 5 (installed 2018) | 97.7 | [5 empty] | UUG0103
United Utilities | WIGAN CEMETERY COMBINED SEWER OV | Wigan Cemetry CSO | 017081356 | WIG0208 | SO | SO on sewer network | SD5873004030 | GB112070061610 | Poolstock Brook | INCE BROOK | N/A | N/A | Not Applicable | Commissioned pre-2016 - full year data expected | 0.42 | 3 | 0.375 | 8 (installed 2015) | 98.63 | [5 empty] | UUG0104
United Utilities | ABRAM HALL COMBINED SEWER OVERFLOW | Abram Hall CSO | 016982904 | WIG0216 | SO | SO on sewer network | SD6055001400 | GB112069064520 | Hey/Borsdane Brook | HEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 306.3 | 36 | 44.75 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0105
United Utilities | ATHERTON RD DETENTION TANK | Atherton Road Detention Tank | 016983228 | WIG0222 | SO | SO on sewer network | SD6256003670 | GB112069064520 | Hey/Borsdane Brook | DOG POOL BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 20.45 | 9 | 8.75 | 4 (installed 2019) | 100 | [5 empty] | UUG0106
United Utilities | INCE CEMETARY CSO | Ince Cemetery CSO | 017081358 | WIG0223 | SO | SO on sewer network | SD5867004010 | GB112070061610 | Poolstock Brook | INCE BROOK | N/A | N/A | Not Applicable | Commissioned pre-2016 - full year data expected | 53.77 | 7 | 0.9 | 8 (installed 2015) | 98.57 | [5 empty] | UUG0107
United Utilities | BEECH HILL LANE CSO 50089 | Beech Hill Lane CSO | 017081372 | WIG0224 | SO | SO on sewer network | SD5630007360 | GB112070064820 | Douglas - Lower | BILLY PIT BROOK LPOOL CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 4.15 | 4 | 5.8 | 5 (installed 2018) | 85.04 | Sensor failure / issue | N/A - Ongoing investigation |  |  |  | UUG0108
United Utilities | REAR OF KEATS AVENUE CSO | Rear of Keats Avenue CSO | 017081380 | WIG0226 | SO | SO on sewer network | SD5734004570 | GB112070061600 | Smithy Brook | SMITHY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 17.37 | 16 | 12.6667 | 3 (installed 2020) | 99.99 | [5 empty] | UUG0109
United Utilities | GEORGE ST CSO | George Street CSO | 016983328 | WIG0227 | SO | SO on sewer network | SD6209003800 | GB112069064520 | Hey/Borsdane Brook | DOG POOL BK,TRB OF BORSDANE BK | N/A | N/A | Not Applicable | Dec 2023 | 20.9 | 38 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0110
United Utilities | LIVERPOOL ROAD (HINDLEY) CSO | Liverpool Road (Hindley) CSO | 016983327 | WIG0228 | SO | SO on sewer network | SD6154003260 | GB112069064520 | Hey/Borsdane Brook | TRIBUTARY OF HEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 6.67 | 12 | 5.75 | 4 (installed 2019) | 96.81 | [5 empty] | UUG0111
United Utilities | 396 ATHERTON ROAD CSO | 396 Atherton Road CSO | 016983329 | WIG0229 | SO | SO on sewer network | SD6266003630 | GB112069064520 | Hey/Borsdane Brook | DOG POOL BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 4.4 | 5 | 4 | 4 (installed 2019) | 100 | [5 empty] | UUG0112
United Utilities | REAR OF 125 BAKER STREET CSO | Rear of 125 Baker Street CSO | 017081381 | WIG0239 | SO | SO on sewer network | SD5747004880 | GB112070061610 | Poolstock Brook | POOLSTOCK BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 72.97 | 36 | 29.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0113
United Utilities | STEVENSON CLOSE (WORSLEY) CSO | Stevenson Close (Worsley) CSO | 017091463 | WIG0242 | SO | SO on sewer network | SD5734004410 | GB112070061600 | Smithy Brook | SMITHY BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0.33333 | 3 (installed 2020) | 100 | [5 empty] | UUG0114
United Utilities | GREENWOOD AVENUE CSO | Greenwood Avenue CSO | EPRAB3991EH | WIG0243 | SO | SO on sewer network | SD5620005774 | GB112070064820 | Douglas - Lower | CLOSE BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 694.93 | 88 | 108.6667 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0115
United Utilities | BILLINGE HIGHER END SPS | Billinge Road/Victoria Street CSO | 017081132 | WIG0245 | SO | SO on sewer network | SD5328003840 | GB112070061600 | Smithy Brook | SMITHY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.57 | 4 | 3.75 | 4 (installed 2019) | 100 | [5 empty] | UUG0116
United Utilities | LOWE MILL LANE (HINDLEY) CSO | Lowe Mill Lane (Hindley) CSO | NPSWQD006473 | WIG0249 | SO | SO on sewer network | SD6193004410 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 12.74 | 22 | 16.6667 | 3 (installed 2020) | 99.99 | [5 empty] | UUG0117
United Utilities | DANES AVENUE CSO | Danes Avenue Combined Sewer Overflow (50112) (WIG0250) | NPSWQD006482 | WIG0250 | SO | SO on sewer network | SD6210004720 | GB112069064520 | Hey/Borsdane Brook | BORSDANE BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1476.97 | 131 | 106.8 | 5 (installed 2018) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0118
United Utilities | POOLSTOCK LANE/HOLT STREET CSO | Poolstock Lane/ Holt Street CSO | EPRQP3420GZ | WIG0253 | SO | SO on sewer network | SD5727903869 | GB112070061600 | Smithy Brook | SMITHY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 3.8 | 2 | 2.3333 | 3 (installed 2020) | 97.09 | [5 empty] | UUG0119
United Utilities | 184 WARRINGTON ROAD CSO | 184 Warrington Road CSO | EPRHB3499NK | WIG0254 | SO | SO on sewer network | SD5671804467 | GB112070064820 | Douglas - Lower | TRIB OF RIVER DOUGLAS VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 100 | [5 empty] | UUG0120
United Utilities | HINDLEY PUMPING STATION 50105 HINDL | Hindley PS | 016920132 | WIG0255 | SO | Storm discharge at pumping station | SD6084002390 | GB112069064520 | Hey/Borsdane Brook | HEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 500.52 | 80 | 34.7143 | 7 (installed 2016) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0121
United Utilities | DEAN WOOD CSO | Dean Wood CSO(49202) (WLN0020) | 017091504 | WLN0020 | SO | SO on sewer network | SD5252005510 | GB112070064820 | Douglas - Lower | DEAN BROOK TRIB OF R DOUGLAS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 819.61 | 121 | 97.2 | 5 (installed 2018) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0122
United Utilities | BARROW-IN-FURNESS WWTW | Barrow-in-Furness Wastewater Treatment Works (BARFU) (017470166) | 017470166 | 17470166 | SO | Inlet SO at WwTW | SD2200068190 | 340 |  | WALNEY CHANNEL | 116 Walney | Walney Biggar Bank; Walney West Shore; Walney Sandy Gap | Not Applicable | Commissioned in 2018 - full year data expected | 571.75 | 30 | 35.4 | 5 (installed 2018) | 68.97 | Telemetry or data archiving failure / issue | N/A - Ongoing investigation |  |  |  | UUG0123
United Utilities | BARROW-IN-FURNESS WWTW | Barrow-in-Furness Wastewater Treatment Works (BARFU) (017470166) | 017470166 | 17470166 | ST | Storm tank at WwTW | SD2200068190 | 340 |  | WALNEY CHANNEL | 116 Walney | Walney Biggar Bank; Walney West Shore; Walney Sandy Gap | Not Applicable | Commissioned in 2018 - full year data expected | 1114.95 | 80 | 51 | 5 (installed 2018) | 99.98 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0124
United Utilities | SCHNEIDER ROAD CSO | Schneider Road CSO | 017480361 | BRW0009 | SO | SO on sewer network | SD1958070871 | 344 |  | ORMSGILL RESERVOIR | 116 - Walney | Walney West Shore | Not Applicable | Commissioned in 2016 - full year data expected | 211.08 | 22 | 63.4286 | 7 (installed 2016) | 98.42 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0125
United Utilities | ASH LANE CSO | Ash Lane | 016920541 | HAL0037 | SO | SO on sewer network | SJ4770085200 | GB112069061390 | Ditton Brook (Halewood to Mersey Estuary) | DITTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 134.91 | 18 | 29.75 | 4 (installed 2019) | 99.56 | [5 empty] | UUG0126
United Utilities | BIGGAR VILLAGE PUMPING STATION | Biggar Village PS | 01BRW0001 | BRW0001 | SO | Storm discharge at pumping station | SD1916066320 | 340 |  | WALNEY CHANNEL | 116 Walney | Walney Biggar Bank; Walney West Shore; Walney Sandy Gap | Not Applicable | Commissioned in 2017 - full year data expected | 2.84 | 2 | 1.8333 | 6 (installed 2017) | 72.21 | Comms failure / issue | Resolved - January after reporting year |  |  |  | UUG0127
United Utilities | AINSLIE ST/HARROGATE ST | Ainslie Street/Harrogate Street CSO | 01BRW0012 | BRW0012 | SO | SO on sewer network | SD1966070551 | 344 |  | ORMSGILL RES | 116 - Walney | Walney West Shore | Not Applicable | Commissioned in 2016 - full year data expected | 10.9 | 38 | 46 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0128
United Utilities | AINSLIE ST OXFORD ST CSO 041A9 | Ainslie Street/Oxford Street CSO | 01BRW0013 | BRW0013 | SO | SO on sewer network | SD1966070550 | 344 |  | ORMSGILL RESERVOIR | 116 - Walney | Walney West Shore | Not Applicable | Commissioned in 2016 - full year data expected | 2.8 | 20 | 30.8571 | 7 (installed 2016) | 100 | [5 empty] | UUG0129
United Utilities | AINSLIE STREET/NEWPORT ST CSO 041A7 | Ainslie Street/Newport Street CSO | 01BRW0011 | BRW0011 | SO | SO on sewer network | SD1966070552 | 344 |  | ORMSGILL RES | 116 - Walney | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0.23 | 2 | 0.83333 | 6 (installed 2017) | 100 | [5 empty] | UUG0130
United Utilities | FREDERICK ST PS | Frederick Street Pumping Station | 017480412 | BRW0044 | SO | Storm discharge at pumping station | SD2123068810 | 340 |  | MILL BECK/ CAVENDISH DOCK | 116 Walney | Walney Biggar Bank; Walney West Shore; Walney Sandy Gap | Not Applicable | Commissioned in 2017 - full year data expected | 168.4 | 25 | 19 | 6 (installed 2017) | 99.96 | [5 empty] | UUG0131
United Utilities | RAMPSIDE PUMPING STATION | Rampside Village PS | 01BRW0071 | BRW0071 | SO | Storm discharge at pumping station | SD2390065800 | 342 |  | MORECAMBE BAY | 117 Roosebeck | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 329.21 | 80 | 57.6667 | 6 (installed 2017) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0132
United Utilities | SPIKE ISLAND ACCESS RD CSO (202RW) | SPIKE ISLAND ACCESS ROAD CSO | 01HAL0053 | HAL0053 | SO | SO on sewer network | SJ5165084740 | GB531206908100 | MERSEY | BOWERS BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 9.8 | 24 | 15 | 3 (installed 2020) | 97.96 | [5 empty] | UUG0133
United Utilities | SOUTH EAST OF NEWTON SSO | SE Newton | 017370140 | BRW0073 | SO | Storm discharge at pumping station | SD2342071280 | 342 |  | SARAH BECK | N/A | N/A | Not Applicable | Dec 2023 | 50.3 | 50 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0134
United Utilities | OXFORD STREET/AINSLIE STREET CSO | Oxford Street/Ainsley Street CSO | 017480304 | BRW0091 | SO | SO on sewer network | SD1966070553 | 344 |  | ORMSGILL RESERVOIR | 116 - Walney | Walney West Shore | Not Applicable | Commissioned in 2016 - full year data expected | 25.7 | 11 | 26.4286 | 7 (installed 2016) | 100 | [5 empty] | UUG0135
United Utilities | FERRY PUMPING STATION SITE ID 04528 | Ferry PS | 017480342 | BRW0099 | SO | Storm discharge at pumping station | SD1878068750 | 169 |  | MASSEY BROOK | 116 Walney | Walney Biggar Bank; Walney West Shore; Walney Sandy Gap | Not Applicable | Commissioned in 2017 - full year data expected | 542.37 | 70 | 55 | 6 (installed 2017) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0136
United Utilities | GRAVING DOCK PUMPING STATION | Graving Dock Pumping Station (Site ID 04525) (BRW0100) | 017480340 | BRW0100 | SO | Storm discharge at pumping station | SD1889069320 | 344 |  | THE WALNEY CHANNEL | 116 Walney | Walney Biggar Bank; Walney West Shore; Walney Sandy Gap | Not Applicable | Commissioned in 2017 - full year data expected | 135 | 143 | 80.5 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0137
United Utilities | TANHOUSE LANE | Tan House Lane/ Moss Bank Road CSO | 01HAL0052 | HAL0052 | SO | SO on sewer network | SJ5274084830 | GB531206908100 | MERSEY | RIVER MERSEY ESTUARY | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0138
United Utilities | WHITEHAVEN WWTW | WHITEHAVEN WwTW | 017480351 | 17480351 | SO | Inlet SO at WwTW | NX9805021130 | GB112074070040 | Lowca Beck | THE IRISH SEA | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 926.59 | 91 | 63 | 4 (installed 2019) | 98.96 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0139
United Utilities | HARBOUR YARD PUMPING STATION | Harbour Yard Pumping Station (Site ID 04524) (BRW0101) | 017480339 | BRW0101 | SO | Storm discharge at pumping station | SD1944067720 | 340 |  | THE WALNEY CHANNEL | 116 Walney | Walney Biggar Bank; Walney West Shore; Walney Sandy Gap | Not Applicable | Commissioned in 2017 - full year data expected | 37.69 | 74 | 53.5 | 6 (installed 2017) | 99.56 |  |  | Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0140
United Utilities | COMMON END COMBINED SEWER OVERFLOW | Common End CSO | 017480427 | COP0003 | SO | SO on sewer network | NY0043022740 | GB112074070040 | Lowca Beck | DISTINGTON BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0141
United Utilities | MILL COTTAGES CSO | MILL COTTAGES CSO | 01COP0024 | COP0024 | SO | SO on sewer network | NY0092023860 | GB112074070040 | Lowca Beck | DISTINGTON BECK | N/A | N/A | Not Applicable | Dec 2023 | 1.8 | 2 |  | <1 yr (installed 2023) | 98.54 | [5 empty] | UUG0142
United Utilities | NEW BRIGHTON PUMPING STATION | New Brighton PS | 016810340 | WIR0130 | SO | Storm discharge at pumping station | SJ3140094200 | 171 |  | TIDAL RIVER MERSEY | N/A | Moreton; Wallasey | Not Applicable | Commissioned in 2017 - full year data expected | 0 | 0 | 1 | 6 (installed 2017) | 100 | [5 empty] | UUG0143
United Utilities | WALLASEY COASTAL DRIVE 51052 | Wallasey Detention Tank | 016983123 | WIR0145 | SO | Storm discharge at pumping station | SJ2945094053 | 351 |  | RIVER MERSEY ESTUARY | N/A | Meols; Moreton; Wallasey | Not Applicable | Commissioned in 2017 - full year data expected | 173.33 | 15 | 5.6667 | 6 (installed 2017) | 79.97 | Telemetry or data archiving failure / issue | N/A - Ongoing investigation |  |  |  | UUG0144
United Utilities | ADELAIDE STREET CSO | Adelaide Street CSO | 016982543 | BOL0025 | SO | SO on sewer network | SD7066007390 | 169 |  | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 540.99 | 100 | 86.2 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0145
United Utilities | HYCEMOOR WWTW BOTHH | BOOTLE / HYCEMOOR WwTW | 017470188 | 17470188 | SO | Inlet SO at WwTW | SD0760090000 | 355 |  | IRISH SEA | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 410.1 | 45 | 49.2 | 5 (installed 2018) | 99.92 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0146
United Utilities | POWERHOUSE ROAD PUMPING STATION | Power House Road PS | 016881966 | WIR0044 | SO | Storm discharge at pumping station | SJ3718080570 | 171 |  | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 350.76 | 86 | 63.6 | 5 (installed 2018) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0147
United Utilities | MAYFIELD DRIVE PS1 CSO 512EZ | Mayfield Drive PS1 CSO (512EZ) | 01WIR0108 | WIR0108 | SO | SO on sewer network | SJ3650081801 | 171 |  | RIVER MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 115.03 | 33 | 59 | 7 (installed 2016) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0148
United Utilities | MAYFIELDS DRIVE WW NTWK PS | Mayfield Drive Ww Ntwk PS | 01WIR0109 | WIR0109 | SO | Storm discharge at pumping station | SJ3650081802 | 171 |  | RIVER MERSEY | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0149
United Utilities | LOWCA BROW (PARTON) CSO | Lowca Brow (Parton) CSO | 017470079 | COP0059 | SO | SO on sewer network | NX9824021200 | GB112074070040 | Lowca Beck | LOWCA BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 109.95 | 64 | 54.6667 | 3 (installed 2020) | 99.31 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0150
United Utilities | ULLGILL MORESBY (MH65) CSO | Ullgill Moresby (MH65) CSO | 017580419 | COP0066 | SO | SO on sewer network | NX9903021260 | GB112074070040 | Lowca Beck | TRIB OF LOWCA BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.1 | 1 | 5.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0151
United Utilities | MORESBY PARKS PS | Moresby Park PS | 017470124 | COP0073 | SO | Storm discharge at pumping station | NY0031018540 | GB112074070030 | Keekle (upper) | BLACKWOOD BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 6.8 | 8 | 8.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0152
United Utilities | EASTHAM VILLAGE CSO | Eastham Village CSO | 01WIR0110 | WIR0110 | SO | SO on sewer network | SJ3650081800 | 171 |  | MERSEY ESTUARY (TIDAL) | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 47.93 | 50 | 40.5714 | 7 (installed 2016) | 99.8 |  |  | Data collection - EDM non-representative location | Resolved - Apr | Other investigation - non-WINEP/Green Recovery | UUG0153
United Utilities | BROMBOROUGH POOL VILLAGE PS 51026 | Bromborough Pool Village PS | 016881615 | WIR0133 | SO | Storm discharge at pumping station | SJ3541084411 | 171 |  | MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 3.68 | 2 | 4.8571 | 7 (installed 2016) | 100 | [5 empty] | UUG0154
United Utilities | HAYES CASTLE FARM CSO (02628) | Rear of Hayes Castle Farm CSO | 017580390 | COP0096 | SO | SO on sewer network | NY0006022370 | GB112074070040 | Lowca Beck | DISTINGTON BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 330.98 | 86 | 78.6667 | 3 (installed 2020) | 76.92 | Sensor failure / issue | Resolved - Jun | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0155
United Utilities | WHITEGATE WWTW | WHITEGATE WwTW | 016810114 | 16810114 | ST | Storm tank at WwTW | SJ6315068970 | GB112068060540 | PETTYPOOL BROOK | Pettypool Brook tributary of River Weaver | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 5 (installed 2018) | 100 | [5 empty] | UUG0156
United Utilities | WHALLEY WASTEWATER TREAMENT WORKS | WHALLEY WwTW | 017180634 | 017160014A | ST | Storm tank at WwTW | SD7200036400 | GB112071065490 | Calder - Pendle Water to conf Ribble | THE RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2260.12 | 152 | 151 | 4 (installed 2019) | 91.76 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0157
United Utilities | RIDDING LANE CSO (342X5) | Ridding Lane Combined Sewage Overflow | 017160332 | RIB0043 | SO | SO on sewer network | SD7235036310 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 865.23 | 104 | 90 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0158
United Utilities | WHALEY BRIDGE STW | WHALEY BRIDGE WwTW | 016940184 | 16940184 | SO | Inlet SO at WwTW | SK0125083220 | GB112069060880 | Goyt (Randall Carr Brook to Sett). | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1708.19 | 99 | 83.6667 | 3 (installed 2020) | 100 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | resolved - oct | Other investigation - non-WINEP/Green Recovery | UUG0159
United Utilities | DISLEY PS | Disley PS | 016982849 | MAC0161 | SO | Storm discharge at pumping station | SJ9812085420 | GB112069060960 | Goyt (Sett to Etherow) | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 768.49 | 116 | 106.3333 | 3 (installed 2020) | 100 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Resolved - Dec | Other investigation - non-WINEP/Green Recovery | UUG0160
United Utilities | WATERSIDE COMBINED SEWER OVERFLOW | Waterside CSO | 016982850 | MAC0164 | SO | SO on sewer network | SJ9810086400 | GB112069060960 | Goyt (Sett to Etherow) | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 68.1 | 14 | 20 | 5 (installed 2018) | 98.48 | [5 empty] | UUG0161
United Utilities | HIGH HILL ROAD CSO | High Hill Road | EPRQB3596AP | PEA0020 | SO | SO on sewer network | SK0078486172 | GB112069060970 | Sett | CULVERTED TRIBUTARY RIVER SETT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 10.87 | 10 | 11.75 | 4 (installed 2019) | 100 | [5 empty] | UUG0162
United Utilities | TORRS DIVERSION CSO 21123 | Torrs Diversion Sewer CSO | 01PEA0023 | PEA0023 | SO | SO on sewer network | SK0011085271 | GB112069060970 | Sett | RIVER GOYT VIS SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 920.03 | 138 | 117.2 | 5 (installed 2018) | 95.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0163
United Utilities | OFLOW 6000 WHALEY BRIDGE CSO 211EA | Overflow 6000 at Whaley Bridge CSO | 01PEA0066 | PEA0066 | SO | SO on sewer network | SK0119081740 | GB112069060880 | Goyt (Randall Carr Brook to Sett). | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 40.1 | 22 | 25.1667 | 6 (installed 2017) | 100 | [5 empty] | UUG0164
United Utilities | WHITE HART INN CSO | White Hart Inn Combined Sewer Overflow | 01PEA0067 | PEA0067 | SO | SO on sewer network | SK0121081350 | GB112069060880 | Goyt (Randall Carr Brook to Sett). | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 53.6 | 13 | 22 | 4 (installed 2019) | 100 | [5 empty] | UUG0165
United Utilities | THE OLD VICARAGE CSO | The Old Vicarage CSO | 016981472 | PEA0068 | SO | SO on sewer network | SK0107080790 | GB112069060860 | Randall Carr Brook | RANDALL CARR BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 1 | 4 (installed 2019) | 100 | [5 empty] | UUG0166
United Utilities | WATFORD BRIDGE CSO 212W1 | Watford Bridge CSO | 016982636 | PEA0074 | SO | SO on sewer network | SK0055086410 | GB112069060970 | Sett | RIVER SETT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 86.03 | 49 | 52.2 | 5 (installed 2018) | 97.02 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0167
United Utilities | GOYT SIDE SPS | Goyt Side PS | 016982416 | PEA0075 | SO | Storm discharge at pumping station | SK0015085100 | GB112069060880 | Goyt (Randall Carr Brook to Sett). | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 17.13 | 26 | 26.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG0168
United Utilities | BATEMILL ROAD CSO | BATEMILL ROAD CSO | 01PEA0044 | PEA0044 | SO | SO on sewer network | SK0094086910 | GB112069060970 | Sett | RIVER SETT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0169
United Utilities | MOUSLEY BOTTOM PS | Mousley Bottom PS | 016982820 | PEA0086 | SO | Storm discharge at pumping station | SJ9930085200 | GB112069060960 | Goyt (Sett to Etherow) | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 78.28 | 21 | 10 | 4 (installed 2019) | 100 | [5 empty] | UUG0170
United Utilities | BRIDGEMONT COMBINED SEWER OVERFLOW | Bridgemont CSO | 016982970 | PEA0090 | SO | SO on sewer network | SK0155082350 | GB112069060880 | Goyt (Randall Carr Brook to Sett). | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 382.37 | 57 | 70.75 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0171
United Utilities | WETHERAL AND GREAT CORBY WWTW WETHE | WETHERAL & GREAT CORBY WwTW | 017670075 | 17670075 | ST | Storm tank at WwTW | NY4673055570 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 29.47 | 20 | 49.1667 | 6 (installed 2017) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0172
United Utilities | GREAT CORBY SYPHON CSO (10C88) | Great Corby Syphon CSO | 01CAR0018 | CAR0018 | SO | SO on sewer network | NY4678055160 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0.6 | 2 | 3.1667 | 6 (installed 2017) | 100 | [5 empty] | UUG0173
United Utilities | WESTHOUGHTON STW | WESTHOUGHTON WwTW | 016950136 | 16950136 | SO | Inlet SO at WwTW | SD6500003660 | GB112069060820 | Westleigh Brook | TRIB OF HALL LEE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 247 | 72 | 74 | 4 (installed 2019) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0174
United Utilities | WESTHOUGHTON STW | WESTHOUGHTON WwTW | 016950136 | 16950136 | ST | Storm tank at WwTW | SD6500003660 | GB112069060820 | Westleigh Brook | TRIB OF HALL LEE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1603.1 | 142 | 145.75 | 4 (installed 2019) | 99.78 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0175
United Utilities | ASHGROVE/SOUTHFIELD DR CSO | Ash Grove/Southfield Drive CSO | 016982976 | BOL0215 | SO | SO on sewer network | SD6454004230 | GB112069060820 | Westleigh Brook | CULVERTED TRIB CUNNINGHAM BRK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 43.67 | 43 | 42.3333 | 3 (installed 2020) | 95.36 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0176
United Utilities | WESTHEAD WWTW | WESTHEAD WwTW | 017030014 | 17030014 | ST | Storm tank at WwTW | SD4414008280 | GB112070064810 | Eller Brook | CASTLE BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1173.5 | 126 | 51.8 | 5 (installed 2018) | 95.35 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0177
United Utilities | BICKERSTAFFE W.WATER PUMP STATION | Bickerstaffe Wastewater PS | 016930107 | WLN0059 | SO | Storm discharge at pumping station | SD4373004370 | GB112069060640 | Downholland (Lydiate/Cheshires Lines) Brook | BICKERSTAFFE BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0178
United Utilities | WESTNEWTON PS WSTNE ALL0114 | Westnewton pumping station (Site ID WSTNE) (ALL0114) | 017580265 | ALL0114 | SO | Storm discharge at pumping station | NY1318043820 | GB112075073660 | Crookhurst Beck | WEST NEWTON BECK | N/A | Allonby | Not Applicable | Commissioned in 2016 - full year data expected | 1322.82 | 111 | 83.1429 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0179
United Utilities | WEETON WASTEWATER TREATMENT WORKS | WEETON WwTW | 017260056 | 17260056 | SO | Inlet SO at WwTW | SD3828034840 | GB112072066120 | Hillylaid Pool - Tidal Wyre | TRIB MAIN DYKE | N/A | Fleetwood | Not Applicable | Commissioned in 2017 - full year data expected | 213.33 | 177 | 115.1667 | 6 (installed 2017) | 99.71 |  |  | Data collection - EDM non-representative location | N/A - Ongoing investigation | U_INV driver - Stage 4: No cost beneficial solution | UUG0180
United Utilities | WEETON WASTEWATER TREATMENT WORKS | WEETON WwTW | 017260056 | 17260056 | ST | Storm tank at WwTW | SD3828034840 | GB112072066120 | Hillylaid Pool - Tidal Wyre | TRIB MAIN DYKE | N/A | Fleetwood | Not Applicable | Commissioned in 2017 - full year data expected | 549.7 | 183 | 120.1667 | 6 (installed 2017) | 100 |  |  | Data collection - EDM non-representative location | N/A - Ongoing investigation | U_INV driver - Stage 4: No cost beneficial solution | UUG0181
United Utilities | WEAVERHAM STW | WEAVERHAM WwTW | 016810113 | 16810113 | SO | Inlet SO at WwTW | SJ6115075180 | GB112068060500 | Weaver (Dane to Frodsham) | TRIB OF RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 26.5 | 17 | 24 | 3 (installed 2020) | 99.39 | [5 empty] | UUG0182
United Utilities | WEAVERHAM STW | WEAVERHAM WwTW | 016810113 | 16810113 | ST | Storm tank at WwTW | SJ6115075180 | GB112068060500 | Weaver (Dane to Frodsham) | TRIB OF RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 9.78 | 4 | 19 | 3 (installed 2020) | 99.98 | [5 empty] | UUG0183
United Utilities | KEEPER'S LANE CSO (472BH) | KEEPERS LANE CSO | 01VRY0081 | VRY0081 | SO | SO on sewer network | SJ6253073360 | GB112068060500 | Weaver (Dane to Frodsham) | TRIB OF RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 6.8 | 5 | 6.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0184
United Utilities | OWLEY WOOD ROAD CSO | OWLEY WOOD ROAD CSO | 01VRY0083 | VRY0083 | SO | SO on sewer network | SJ6255074270 | GB112068060500 | Weaver (Dane to Frodsham) | RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.53 | 6 | 28.6 | 5 (installed 2018) | 100 | [5 empty] | UUG0185
United Utilities | (IN SCOUT HUT) OWLEY WOOD ROAD CSO | (In Scout Hut) Owley Road CSO | 01VRY0096 | VRY0096 | SO | SO on sewer network | SJ6250074270 | GB112068060500 | Weaver (Dane to Frodsham) | RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 100 | [5 empty] | UUG0186
United Utilities | APPLEGARTH | Moor Lane PS / Rowton A41 CSO | 01CHE0023 | CHE0023 | SO | Storm discharge at pumping station | SJ4473064730 | GB111067056930 | Finchetts Gutter | CALDY BROOK RIVER DEE | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 63.17 | 7 | 18.5 | 6 (installed 2017) | 96.52 | [5 empty] | UUG0187
United Utilities | HAYTON PUMPING STATION | Hayton PS | 017680324 | CAR0079 | SO | Storm discharge at pumping station | NY5048057930 | GB102076073981 | Irthing DS Crammel Linn Waterfall | BYE GILL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.01 | 2 | 5.8 | 5 (installed 2018) | 100 | [5 empty] | UUG0188
United Utilities | LITTLE CORBY PS | Little Corby PS | 017680327 | CAR0082 | SO | Storm discharge at pumping station | NY4765057340 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 7.64 | 10 | 6 | 4 (installed 2019) | 99.96 | [5 empty] | UUG0189
United Utilities | NEWBY EAST WASTEWATER NETWORK PS | Newby East PS | 017680329 | CAR0084 | SO | Storm discharge at pumping station | NY4750058050 | GB112069061000 | Irthing DS Crammel Linn Waterfall | RIVER IRTHING VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 380.85 | 83 | 82.8 | 5 (installed 2018) | 99.21 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0190
United Utilities | WARWICK BRIDGE PS | Warwick Bridge PS | 017680331 | CAR0086 | SO | Storm discharge at pumping station | NY4737056940 | GB102076073900 | Trout Beck (Cairn Beck) | CAIRN BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 17.87 | 19 | 20.75 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0191
United Utilities | WARWICK ON EDEN PS | Warwick on Eden PS | 017680330 | CAR0085 | SO | Storm discharge at pumping station | NY4696056660 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0192
United Utilities | ST PAULS ROAD CSO | St Pauls Road CSO | 017190769 | WIR0138 | SO | SO on sewer network | SJ3346087300 | 176 |  | RIVER RIBBLE ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 152.77 | 60 | 67.7143 | 7 (installed 2016) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0193
United Utilities | THE DELL COMBINED SEWER OVERFLOW | The Dell CSO | 016881648 | WIR0139 | SO | SO on sewer network | SJ3417086368 | 171 |  | THE MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 234.25 | 95 | 103 | 7 (installed 2016) | 99.54 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0194
United Utilities | 3 PARK ROAD CSO | No 3 Park Road CSO | 016982965 | WIR0140 | SO | SO on sewer network | SJ3718080580 | 171 |  | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Dec 2023 | 0 | 0 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0195
United Utilities | GREETY GATE PUMPING STATION | Greety Gate PS | 017480364 | LAK0098 | SO | Storm discharge at pumping station | SD2030186811 | 187 |  | DUDDON ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 456.64 | 46 | 28.5 | 4 (installed 2019) | 94.91 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation |  | UUG0196
United Utilities | GREEN DRAGON HOTEL CSO 481EC | GREEN DRAGON HOTEL CSO | 01WAR0067 | WAR0067 | SO | SO on sewer network | SJ7021088750 | GB112069061382 | Bollin (Ashley Mill to Manchester Ship Canal) | RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 240.57 | 35 | 31.2 | 5 (installed 2018) | 100 | [5 empty] | UUG0197
United Utilities | BURGH-BY-SANDS WWTW | BURGH BY SANDS WwTW | 017670208 | 17670208 | SO | Inlet SO at WwTW | NY3185059230 | 89 |  | TRIB RIDDING SOUGH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 199.68 | 34 | 35 | 4 (installed 2019) | 100 | [5 empty] | UUG0198
United Utilities | LONGBURGH PUMPING STATION | Longburgh PS | 017670207 | CAR0044 | SO | Storm discharge at pumping station | NY3090059120 | 89 |  | RIDDING SOUGH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 562.04 | 97 | 98.25 | 4 (installed 2019) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0199
United Utilities | ST NICHOLAS LANE PUMPING STATION | St Nicholas Lane Pumping Station (Site ID STNIC) (LAN0057) | 017190855 | LAN0057 | SO | Storm discharge at pumping station | SD4782068760 | 185 |  | MILL DAM | 115 Morecambe Bay East | Morecambe North; Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 82.82 | 49 | 29.5 | 6 (installed 2017) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0200
United Utilities | LARBURNUM PARK PUMPING STATION | Hope Terrace PS | NPSWQD011002 | LAN0061 | SO | Storm discharge at pumping station | SD4915069680 | 185 |  | BLACK DIKE, TRIB KEER ESTUARY | 115 Morecambe Bay East | Morecambe North | Not Applicable | Commissioned in 2017 - full year data expected | 40.19 | 21 | 21.8333 | 6 (installed 2017) | 94.64 | [5 empty] | UUG0201
United Utilities | OUGHTRIGHTON LANE CSO 482KO | Oughtrington Lane CSO | 016982896 | WAR0115 | SO | SO on sewer network | SJ6969087430 | GB112069061382 | Bridgewater Canal | BRIDGEWATER CANAL | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 1.07 | 5 | 5.3333 | 6 (installed 2017) | 100 | [5 empty] | UUG0202
United Utilities | CRAG BANK PUMPING STATION | Crag Bank PS | 017280249 | LAN0062 | SO | Storm discharge at pumping station | SD4871070000 | 185 |  | TRIB BLACK DYKE | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 23.97 | 5 | 4.8333 | 6 (installed 2017) | 97.79 | [5 empty] | UUG0203
United Utilities | HEST BANK PUMPING STATION | Hest Bank PS | 017290499 | LAN0120 | SO | Storm discharge at pumping station | SD4684066860 | 185 |  | HATLEX BECK | 115 Morecambe Bay East | Morcambe North | Not Applicable | Commissioned in 2017 - full year data expected | 131.98 | 20 | 21.5 | 6 (installed 2017) | 99.98 | [5 empty] | UUG0204
United Utilities | MILL LANE CSO 425E6 | Mill Lane CSO | 01STH0049 | STH0049 | SO | SO on sewer network | SJ8837061520 | GB112068055360 | Millingford (Newton) Brook | Newton Brook | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.57 | 4 | 46.6667 | 3 (installed 2020) | 86 | Comms failure / issue | Resolved - January after reporting year | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0205
United Utilities | WHARF ROAD CSO 42077 | Wharf Road CSO | 01STH0070 | STH0070 | SO | SO on sewer network | SJ5658094770 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | SANKEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 195.25 | 59 | 74.8 | 5 (installed 2018) | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0206
United Utilities | RED BROW CSO (42076) | Red Brow Wood CSO | NPSWQD010717 | STH0071 | SO | SO on sewer network | SJ5770494436 | GB112069061220 | Millingford (Newton) Brook | SANKEY CANAL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 322.2 | 76 | 70.3333 | 3 (installed 2020) | 99.72 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0207
United Utilities | LODGE LANE COMBINED SEWER OVERFLOW | Lodge Lane (Near Ellams Brook) CSO | 016920211 | STH0072 | SO | SO on sewer network | SJ5817096900 | GB112069061220 | Millingford (Newton) Brook | TRIB DEAN DAM | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 430.81 | 43 | 56.75 | 4 (installed 2019) | 95.58 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0208
United Utilities | 10 WARWICK AVENUE CSO (42058) | 10 Warwick Avenue CSO | 016920445 | STH0075 | SO | SO on sewer network | SJ5901094760 | GB112069061220 | Millingford (Newton) Brook | NEWTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 487.02 | 80 | 73.3333 | 3 (installed 2020) | 97.73 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0209
United Utilities | PARK ROAD NORTH | Park Road North | 01STH0076 | STH0076 | SO | SO on sewer network | SJ5913095410 | GB112069061220 | Millingford (Newton) Brook | Millingford (Newton) Brook | N/A | N/A | Not Applicable | Dec 2023 | 3134.2 | 176 |  | <1 yr (installed 2023) | 97.6415 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0210
United Utilities | WHARF ROAD CSO | Wharf Road | 01STH0109 | STH0109 | SO | SO on sewer network | SJ5656094750 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | SANKEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 2.6 | 5 (installed 2018) | 100 | [5 empty] | UUG0211
United Utilities | PENKFORD BRIDGE | Penkford Bridge | 01STH0110 | STH0110 | SO | SO on sewer network | SJ5622094900 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | Sankey Brook | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 10.17 | 21 | 35.25 | 4 (installed 2019) | 99.73 | [5 empty] | UUG0212
United Utilities | WEST END/ WHARF ROAD CSO 425F3 | West End Wharf Road CSO | 016982990 | STH0113 | SO | SO on sewer network | SJ5665094800 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | SANKEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 81.37 | 39 | 25.4 | 5 (installed 2018) | 100 | [5 empty] | UUG0213
United Utilities | WARGRAVE ROAD CSO | Wargrave Road CSO | NPSWQD004566 | STH0123 | SO | SO on sewer network | SJ5901194760 | GB112069061220 | Millingford (Newton) Brook | NEWTON BROOK | N/A | N/A | Not Applicable | Dec 2023 | 3102.27 | 205 |  | <1 yr (installed 2023) | 99.5595 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0214
United Utilities | CAUSEWAY PS | Causeway Pumping Station | 01WAR0005 | WAR0005 | SO | Storm discharge at pumping station | SJ6068087600 | GB531206908100 | MERSEY | River Mersey | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1.93 | 9 | 8 | 3 (installed 2020) | 100 | [5 empty] | UUG0215
United Utilities | COCKERHAM CSO | Cockerham Adjacent to Manor Inn Car Park CSO | 017280280 | LAN0081 | SO | SO on sewer network | SD4520051300 | 343 |  | TRIB RIVER COCKER | 114 Lune | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 919.6 | 154 | 155.3333 | 6 (installed 2017) | 96.4 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0216
United Utilities | PENNINGTON LANE CSO | Pennington Lane CSO | EPRSB3399EK | WAR0008 | SO | SO on sewer network | SJ5556893645 | GB112069061170 | Sutton Brook | SANKEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.43 | 4 | 91 | 3 (installed 2020) | 91.22 |  |  | Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0217
United Utilities | CRAKE VALLEY WWTW | CRAKE VALLEY WwTW | EPRFP3828GS | EPRFP3828GS | SO | Inlet SO at WwTW | SD3141682708 | 181 |  | RIVER CRAKE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 192.85 | 71 | 56.4 | 5 (installed 2018) | 98.32 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0218
United Utilities | ORFORD PARK CSO 48087 | Orford Park CSO | NPSWQD010762 | WAR0014 | SO | Storm discharge at pumping station | SJ6113789997 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | LONGFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 598.89 | 85 | 69.6 | 5 (installed 2018) | 99.73 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0219
United Utilities | ATHLONE ROAD CSO 48062 | Athlone Road CSO | 016920452 | WAR0016A | SO | SO on sewer network | SJ6037090071 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | LONGFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 5 (installed 2018) | 100 | [5 empty] | UUG0220
United Utilities | LONGFORD BARRAGE CSO 48008 | Longford Barrage CSO | EPRHB3795RH | WAR0016 | SO | SO on sewer network | SJ6038690068 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | LONGFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 169.49 | 25 | 38.8 | 5 (installed 2018) | 100 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG0221
United Utilities | KINGSWAY COMBINED SEWER OVERFLOW | Kingsway CSO | 016920069 | WAR0017 | SO | SO on sewer network | SJ6245088010 | GB112069061012 | Mersey (Bollin confluence to Howley Weir) including Padgate Brook | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 98.6 | 93 | 99.5714 | 7 (installed 2016) | 90.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0222
United Utilities | MILL LANE/WINWICK RD SSO | Junction of Mill Lane & Winwick Road CSO | 016920072 | WAR0018 | SO | SO on sewer network | SJ6017091370 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | MILL BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 47.69 | 17 | 16.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0223
United Utilities | GREENODD PUMPING STATION | Greenodd Sewage Pumping Station (Site ID 398CS, GREEN ) (LAK0109) | EPRFP3828XR | LAK0109 | SO | Storm discharge at pumping station | SD3148082410 | 181 |  | RIVER LEVEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1095.59 | 88 | 70.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0224
United Utilities | PADDINGTON PS 48028 | Paddington PS | 01WAR0030 | WAR0030 | SO | Storm discharge at pumping station | SJ6381088930 | GB112069061012 | Mersey (Bollin confluence to Howley Weir) including Padgate Brook | RIVER MERSEY | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0225
United Utilities | WARRINGTON ROAD PS | Warrington Road (Risley) PS | 01WAR0031 | WAR0031 | SO | Storm discharge at pumping station | SJ6392092540 | GB112069061020 | Spittle Brook | UNNAMED TRIBUTARY CROSS BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 86.89 | 22 | 25 | 3 (installed 2020) | 99.45 | [5 empty] | UUG0226
United Utilities | BEWSEY BRIDGE PUMPING STN | Bewsey Bridge PS | NPSWQD006951 | WAR0034 | SO | Storm discharge at pumping station | SJ5923089440 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | Sankey Brook | N/A | N/A | Not Applicable | Commissioned pre-2016 - full year data expected | 0 | 0 | 0 | 8 (installed 2015) | 100 | [5 empty] | UUG0227
United Utilities | LODGE LANE COMBINED SEWER OVERFLOW | Lodge Lane, Bewsey CSO | 016993698 | WAR0035 | SO | SO on sewer network | SJ5817096900 | GB112069061220 | Millingford (Newton) Brook | ELLAMS BROOK,TRIB NEWTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 151.3 | 42 | 33.6667 | 3 (installed 2020) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0228
United Utilities | CROSSCANONBY WWTW CROSC | CROSSCANONBY WwTW | 017570086 | 17570086 | ST | Storm tank at WwTW | NY0649038840 | 357 |  | SCAD BECK | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 1553.65 | 109 | 50.4286 | 7 (installed 2016) | 99.29 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | U_INV driver - Stage 4: No cost beneficial solution | UUG0229
United Utilities | 6 SANDY LANE WEST (LONGFORD) CSO | 6 Sandy Lane West (Longford) CSO | 01WAR0050 | WAR0050 | SO | SO on sewer network | SJ6019090831 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | MILL BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 29.5 | 5 | 6.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG0230
United Utilities | GOUGH AVENUE/SANDY LANE WEST CSO | Junction Sandy Lane/ Bough Avenue CSO | 01WAR0051 | WAR0051 | SO | SO on sewer network | SJ6019090830 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | MILL BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 39.5 | 10 | 12.3333 | 3 (installed 2020) | 99.99 | [5 empty] | UUG0231
United Utilities | EASTLAND FARM COMBINED SEWER O'FLOW | Eastland Farm CSO | 01ALL0017 | ALL0017 | SO | SO on sewer network | NY0742039190 | 357 |  | SCAD BECK TRIB OF SOLWAY EST'Y | N/A | Allonby South | Not Applicable | Commissioned in 2016 - full year data expected | 93.47 | 86 | 103 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP or Green Recovery | UUG0232
United Utilities | WHARF STREET CSO | Wharf Street CSO | 01WAR0061 | WAR0061 | SO | SO on sewer network | SJ6084087870 | GB112069061012 | Mersey (Bollin confluence to Howley Weir) including Padgate Brook | RIVER MERSEY | N/A | N/A | Not Applicable | Dec 2023 | 0 | 0 |  | <1 yr (installed 2023) | 42.5824 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0233
United Utilities | LONGSHAW STREET CSO (48066) | Longshaw Street CSO | 016993702 | WAR0066 | SO | SO on sewer network | SJ5989089940 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | SANKEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 77.58 | 13 | 16 | 3 (installed 2020) | 60.46 | Comms failure / issue | Resolved - Nov |  |  |  | UUG0234
United Utilities | ELLESMERE PORT WWTW | ELLESMERE PORT WwTW | 016810030 | 16810030 | ST | Storm tank at WwTW | SJ4320074650 | 168 |  | THORNTON BROOK/RIVER GOWY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 710.89 | 91 | 85.5 | 4 (installed 2019) | 99.91 |  |  | Data collection - EDM non-representative location | Resolved - Apr | Other investigation - non-WINEP/Green Recovery | UUG0235
United Utilities | JUNC ALDER LANE/NORTH AVE CSO | Junction Alder Lane/North Avenue CSO | 016993626 | WAR0074 | SO | SO on sewer network | SJ6085090020 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | LONGFORD BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 1.6667 | 3 (installed 2020) | 95.34 | [5 empty] | UUG0236
United Utilities | 4 TAVLIN AVENUE CSO | 4 Tavlin Avenue CSO | 016993627 | WAR0076 | SO | SO on sewer network | SJ5992089940 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | DALLAM BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 3.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG0237
United Utilities | WARRINGTON ROAD WA5 2JL CSO | The Warrington Road CSO | 016993441 | WAR0080 | SO | SO on sewer network | SJ5727087730 | GB112069060990 | Whittle Brook (Mersey Estuary) | WHITTLE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 6.08 | 18 | 19.75 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0238
United Utilities | HIGHFIELD AVENUE CSO | Highfield Avenue CSO | 016982697 | WAR0105 | SO | SO on sewer network | SJ5712088130 | GB112069060990 | Whittle Brook (Mersey Estuary) | TRIB WHITTLE BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 15.23 | 11 | 11.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG0239
United Utilities | MILL HOUSE LANE CSO | Mill House Lane CSO | 016982895 | WAR0117 | SO | SO on sewer network | SJ6392092570 | GB112069061020 | Spittle Brook | TRIB COCK SHOT BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 117.73 | 56 | 43.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0240
United Utilities | WESTY FLUMES 1 SOUTH CSO 489CB | Westy Flumes (1) South CSO | 016982974 | WAR0125 | SO | SO on sewer network | SJ6282088380 | GB112069061012 | Mersey (Bollin confluence to Howley Weir) including Padgate Brook | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 325.57 | 74 | 24.6 | 5 (installed 2018) | 90.66 |  |  | Data collection - EDM non-representative location | Resolved - Feb | Other investigation - non-WINEP/Green Recovery | UUG0241
United Utilities | PRINCESS RD (PETER ST) CSO (50006) | Princess Road (St.Peter) CSO | 016983355 | WIG0037 | SO | SO on sewer network | SJ5861098950 | GB112069061220 | Millingford (Newton) Brook | MILLINGFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 73.87 | 48 | 36.6667 | 3 (installed 2020) | 99.89 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0242
United Utilities | TROUTBECK ROAD CSO 508B3 | Troutbeck Road CSO | 016983357 | WIG0105 | SO | SO on sewer network | SJ5455098970 | GB112069061230 | Black Brook (Mersey Estuary) | MILLINGFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 1 | 5 (installed 2018) | 100 | [5 empty] | UUG0243
United Utilities | CLEVELAND DRIVE CSO | Cleveland Drive CSO | 016983353 | WIG0106 | SO | SO on sewer network | SJ5854499576 | GB112069061220 | Millingford (Newton) Brook | MILLINGFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 127.22 | 64 | 49.75 | 4 (installed 2019) | 99.2 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0244
United Utilities | PS AT BRYN GATES | Bryn Gates PS | 01WIG0117 | WIG0117 | SO | Storm discharge at pumping station | SD5947000900 | GB112069064520 | Hey/Borsdane Brook | Hey/Borsdane Brook | N/A | N/A | Not Applicable | Dec 2023 | 0 | 0 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0245
United Utilities | NR FOOTBRIDGE OVER BRK | Monmouth Crescent | 01WIG0119 | WIG0119 | SO | SO on sewer network | SJ5862698924 | GB112069061220 | Millingford (Newton) Brook | Millingford (Newton) Brook | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0246
United Utilities | MILL LANE (GOLBORNE) CSO | Mill Lane (Golborne) CSO | 016983354 | WIG0147 | SO | SO on sewer network | SJ6060097290 | GB112068055360 | Millingford (Newton) Brook | Newton Brook | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 132.33 | 25 | 44 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0247
United Utilities | LANDGATE SPS | Landgate PS | 017020034 | WIG0154 | SO | Storm discharge at pumping station | SD5715001450 | GB112070061610 | Poolstock Brook | PARK BROOK | N/A | N/A | Not Applicable | Dec 2023 | 1.39 | 1 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0248
United Utilities | CRANBERRY LODGE PUMPING STATION | Cranberry Lodge Pumping Station (Site ID 50003) (WIG0162) | 01WIG0162 | WIG0162 | SO | Storm discharge at pumping station | SD5698001890 | GB112070061610 | Poolstock Brook | PARK BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 10.5 | 7 | 5.2 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0249
United Utilities | MANHOLE ON SYPHON (WARCOP) CSO | Manhole on Syphon (Warcop) CSO | 01EDE0023 | EDE0023 | SO | SO on sewer network | NY7475015440 | GB102076070750 | Low Gill (Crooks Beck) | CROOKS BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 596.67 | 81 | 75.3333 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0250
United Utilities | Warcop Village PS | Warcop Village PS | 17670043 | EDE0070 | SO | Storm discharge at pumping station | NY7462015390 | GB102076070750 | Low Gill (Crooks Beck) | Low Gill (Crooks Beck) | N/A | N/A | Not Applicable | Dec 2023 | 747.65 | 87 |  | <1 yr (installed 2023) | 100 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0251
United Utilities | WHITBY ROAD COMBINED SEWER OVERFLOW | Whitby Road CSO | 016881598 | ELL0032 | SO | SO on sewer network | SJ4097077103 | 171 |  | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 4 | 4 (installed 2019) | 100 | [5 empty] | UUG0252
United Utilities | KERN MILL LANE CSO 122BI | Kem Mill Lane CSO | 017060027 | CHR0060 | SO | SO on sewer network | SD5769021680 | GB112070064911 | Lostock US Farington Weir | RIVER LOSTOCK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 81.97 | 36 | 41.8 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0253
United Utilities | OFF BRIDGE ST | Off Bridge Street PS | 01CHR0032 | CHR0032 | SO | Storm discharge at pumping station | SD6002021410 | GB112070064911 | Lostock US Farington Weir | KENYON BROOK | N/A | N/A | Not Applicable | Dec 2023 | 250.24 | 18 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0254
United Utilities | MH Y6 HAVELOCK ROAD CSO | MH Y6 Havelock Road CSO | 017060092 | SRI0006 | SO | SO on sewer network | SD5615025440 | GB112070064911 | Lostock US Farington Weir | RIVER LOSTOCK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 312.83 | 34 | 17.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG0255
United Utilities | FAIRFIELD STREET CSO | Fairfield Street CSO | 017060093 | SRI0007 | SO | SO on sewer network | SD5481025110 | GB112070064911 | Lostock US Farington Weir | RIVER LOSTOCK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 13.9 | 11 | 8.3333 | 3 (installed 2020) | 99.86 | [5 empty] | UUG0256
United Utilities | CANN BRIDGE STREET CSO 40042 | Cann Bridge Street CSO | 017160142 | SRI0008 | SO | SO on sewer network | SD5758027610 | GB112071065300 | Darwen - conf Roddlesworth to tidal | RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 62.43 | 35 | 93.8 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0257
United Utilities | DUDDLE LANE CSO | Duddle Lane CSO | 017180617 | SRI0010 | SO | SO on sewer network | SD5599026920 | GB112071065300 | Darwen - conf Roddlesworth to tidal | HENNEL BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 76.53 | 11 | 9.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0258
United Utilities | TOWN PUMPING STATION | Town PS | 016881718 | ELL0035 | SO | Storm discharge at pumping station | SJ4095077100 | 171 |  | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 266.09 | 36 | 86.25 | 4 (installed 2019) | 89.29 | Sensor failure / issue | Resolved - Nov | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0259
United Utilities | HARROWSIDE PUMPING STATION | Harrowside Pumping Station | 017180568 | BPL0003 | SO | Storm discharge at pumping station | SD3063132517 | 350 |  | IRISH SEA | N/A | Blackpool North; Blackpool Central; Blackpool South | Not Applicable | Commissioned in 2017 - full year data expected | 0 | 0 | 0.16667 | 6 (installed 2017) | 99.99 | [5 empty] | UUG0260
United Utilities | DAUB HALL LANE CSO 403CW | Daub Hall Lane, Walton-le-Dale CSO | 01LA1606 | SRI0015 | SO | SO on sewer network | SD5910027280 | GB112071065280 | Many Brooks | BLACK BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 411.2 | 107 | 91.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0261
United Utilities | CHATSWORTH AVENUE SPS | Chatsworth Avenue PS | 017260171 | BPL0038 | SO | Storm discharge at pumping station | SD3116046680 | 349 |  | IRISH SEA | 113 Lune | Bispham; Cleveleys; Fleetwood | Not Applicable | Commissioned in 2017 - full year data expected | 103.75 | 43 | 54.8333 | 6 (installed 2017) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0262
United Utilities | CUERDALE LANE CSO 401QM | CUERDALE LANE CSO | 01SRI0026 | SRI0026 | SO | SO on sewer network | SD5654028480 | GB112071065500 | Ribble - conf Calder to tidal | RIVER RIBBLE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.2 | 2 | 1.6 | 5 (installed 2018) | 96.85 | [5 empty] | UUG0263
United Utilities | FIELD EAST OF RIVER DARWIN CSO | Field East of River Darwin CSO | 017190837 | SRI0028 | SO | SO on sewer network | SD5585027830 | GB112071065300 | Darwen - conf Roddlesworth to tidal | RIVER DARWIN | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 735.7 | 120 | 103.2857 | 7 (installed 2016) | 96.93 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0264
United Utilities | GYNN SQUARE | Gynn Square CSO | 017180573 | BPL0035 | SO | SO on sewer network | SD3060037800 | 349 |  | IRISH SEA | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0265
United Utilities | REAR OF LUNAR CARAVANS | Rear of Lunar Caravans CSO | 017081263 | SRI0055 | SO | SO on sewer network | SD5481025120 | GB112070064911 | Lostock US Farington Weir | RIVER LOSTOCK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 33.97 | 27 | 28.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0266
United Utilities | BROWNEDGE LANE CSO 401GR | Brownedge Lane CSO | 017180538 | SRI0058 | SO | SO on sewer network | SD5633026290 | GB112071065300 | Darwen - conf Roddlesworth to tidal | COCKSHOTT BK TRB R DARWEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 10.27 | 8 | 4.2 | 5 (installed 2018) | 100 | [5 empty] | UUG0267
United Utilities | WADDINGTON WWTW | WADDINGTON WwTW | 017160048 | 17160048 | ST | Storm tank at WwTW | SD7230043050 | GB112071065520 | Bashall Brook | BASHALL BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 3624.35 | 212 | 206 | 4 (installed 2019) | 99.16 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0268
United Utilities | SPRING GARDENS WADDINGTON CSO | Spring Gardens(Waddington) CSO | 01RIB0004 | RIB0004 | SO | SO on sewer network | SD7306043500 | GB112071065612 | Ribble DS Stock Beck | WADDINGTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 180.97 | 85 | 74.5 | 4 (installed 2019) | 98.15 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0269
United Utilities | URMSTON WASTEWATER TREATMENT WORKS | URMSTON WwTW | 016940154 | 16940154 | ST | Storm tank at WwTW | SJ7287093990 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1790.37 | 153 | 162.2 | 5 (installed 2018) | 99.95 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0270
United Utilities | CARRINGTON LANE | Carrington Road Bridge CSO | 016993623 | TRA0001 | SO | SO on sewer network | SJ7420093770 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 10.67 | 6 | 6.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0271
United Utilities | WESTERN ROAD CSO | WESTERN ROAD CSO | 01TRA0002 | TRA0002 | SO | SO on sewer network | SJ7419094330 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | CARRS DITECH (CULVERT) | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2.6 | 9 | 31.4 | 5 (installed 2018) | 99.97 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG0272
United Utilities | CARRINGTON RD | Carrington Road PS | 01TRA0024 | TRA0024 | SO | Storm discharge at pumping station | SJ7439093820 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 522.22 | 82 | 68 | 4 (installed 2019) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0273
United Utilities | CHURCH ROAD | Urmston Sewerage, Church Road & Carrington Road PS | 01TRA0025 | TRA0025 | SO | Storm discharge at pumping station | SJ7483093740 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | River Mersey | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0274
United Utilities | TOWNSGATE COMBINED SEWER OVERFLOW | TOWNSGATE CSO | 01TRA0037 | TRA0037 | SO | SO on sewer network | SJ7288094050 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 592.2 | 118 | 113.6667 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0275
United Utilities | LYTHAM ROAD CSO (452EF) | LYTHAM ROAD CSO | 01TRA0038 | TRA0038 | SO | SO on sewer network | SJ7314094870 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 34.77 | 27 | 26.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0276
United Utilities | Flixton Road/Irlam Road Flixton Combined Sewer Overflow (451UM) (TRA0039) | Flixton Road/Irlam Road Flixton Combined Sewer Overflow (451UM) (TRA0039) | 16993651 | TRA0039 | SO | SO on sewer network | SJ7449093850 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | River Mersey via surface water sewer | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 79.53 | 44 | 9 | 5 (installed 2018) | 99.98 |  |  | Data collection - EDM non-representative location | Resolved - Sep |  | UUG0277
United Utilities | FLIXTON ROAD CSO | Flixton Road CSO | 016993652 | TRA0040 | SO | SO on sewer network | SJ7449093850 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 9.7 | 8 | 22.6 | 5 (installed 2018) | 100 | [5 empty] | UUG0278
United Utilities | LIME TREE CLOSE CSO | Lime Tree Close CSO | 016940381 | TRA0071 | SO | SO on sewer network | SJ7714093810 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 26.21 | 15 | 14 | 3 (installed 2020) | 60.16 | Sensor failure / issue | Resolved - Jul |  |  |  | UUG0279
United Utilities | ULVERSTON WWTW | ULVERSTON WwTW | 017370179 | 17370179 | SO | Inlet SO at WwTW | SD3071077240 | GB112073071160 | Dragley Beck | ULVERSTON CHANNEL/ CARTER POOL | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 4.61 | 22 | 3.6667 | 6 (installed 2017) | 100 | [5 empty] | UUG0280
United Utilities | ROSSALL SCHOOL PUMPING STATION | Rossall School PS | 01WYR0007 | WYR0007 | SO | Storm discharge at pumping station | SD3172045110 | 341 |  | UNNAMED DYKE | N/A | Cleveleys | Not Applicable | Commissioned in 2016 - full year data expected | 1.26 | 6 | 3.1429 | 7 (installed 2016) | 99.99 | [5 empty] | UUG0281
United Utilities | TOWN BECK CSO 39065 | Town Beck CSO | 017380295 | LAK0059 | SO | SO on sewer network | SD2918078120 | GB112073071160 | Dragley Beck | TOWN BECK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 95.27 | 47 | 18 | 6 (installed 2017) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0282
United Utilities | OAKWOOD DRIVE CROFTLANDS CSO | Oakwood Drive (Croftlands) Combined Sewer Overflow | 017380296 | LAK0058 | SO | SO on sewer network | SD2907277209 | GB112073071160 | Dragley Beck | DRAGLEY BECK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0 | 0 | 38.8333 | 6 (installed 2017) | 100 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG0283
United Utilities | COOPER LANE SPS | Cooper Lane Pumping Station (Site ID 39056) (LAK0092) | 017280253 | LAK0092 | SO | Storm discharge at pumping station | SD3085074800 | GB531207311900 | LEVEN | LEVEN ESTUARY | 129 Morecambe Bay | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 471.54 | 31 | 18.1667 | 6 (installed 2017) | 99.71 | [5 empty] | UUG0284
United Utilities | BLACKPOOL OLD ROAD CSO | Blackpool Old Road CSO | 017290529 | WYR0018 | SO | SO on sewer network | SD3372038940 | 180 |  | HORSEBRIDGE DYKE, TRIB OF MAIN | N/A | St Annes; St Annes North | Not Applicable | Commissioned in 2016 - full year data expected | 66.17 | 21 | 51 | 7 (installed 2016) | 97.95 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0285
United Utilities | TYLDESLEY STW | TYLDESLEY WwTW | 016920135 | 16920135 | ST | Storm tank at WwTW | SJ6959099000 | GB112069061100 | Astley Brook (Mersey) | MOSS BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 659.13 | 43 | 80.5 | 4 (installed 2019) | 48.01 | Comms failure / issue | Resolved - January after reporting year | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0286
United Utilities | EAST LANCS ROAD PUMPING STATION | East Lancs Road Pumping Station (EASTL) (WIG0179) | 01WIG0179 | WIG0179 | SO | Storm discharge at pumping station | SD6992000140 | GB112069061100 | Astley Brook (Mersey) | ASTLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 30.61 | 39 | 59.8 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0287
United Utilities | PARR BRIDGE/MOSLEY COMMON RD CSO | Parr Bridge/Mosley Common Road CSO | 016982787 | WIG0209 | SO | SO on sewer network | SD7137001500 | GB112069061100 | Astley Brook (Mersey) | HONKSFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 10.83 | 13 | 24.75 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0288
United Utilities | TORVER STW | TORVER WwTW | 017370039 | 17370039 | SO | Inlet SO at WwTW | SD2817093930 | GB112073071200 | Torver Beck | TORVER BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 376.17 | 103 | 34.3333 | 3 (installed 2020) | 99.97 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0289
United Utilities | TORPENHOW WWTW (TORPE) | TORPENHOW WwTW | 017570075 | 17570075 | SO | Inlet SO at WwTW | NY2075040410 | GB112075073600 | Cockshot Beck | COCKSHOT BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 553.81 | 116 | 144.5 | 4 (installed 2019) | 99.96 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0290
United Utilities | TINTWISTLE STW | TINTWISTLE WwTW | 016940183 | 16940183 | ST | Storm tank at WwTW | SK0176096770 | GB112069060780 | Etherow (Woodhead Res. to Glossop Bk.) | RIVER ETHEROW | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 2521.5 | 202 | 169.6667 | 3 (installed 2020) | 100 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0291
United Utilities | WOODLANDS CLOSE CSO (21117) | Woodlands Close CSO | 01PEA0042 | PEA0042 | SO | SO on sewer network | SK0167096890 | GB112069060780 | Etherow (Woodhead Res. to Glossop Bk.) | RIVER ETHEROW | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 772.71 | 133 | 113.3333 | 3 (installed 2020) | 96.62 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0292
United Utilities | BANK LANE TINTWISTLE CSO | Bank Lane (Tintwistle) Combined Sewer Overflow | 01PEA0043 | PEA0043 | SO | SO on sewer network | SK0206096980 | GB112069060780 | Etherow (Woodhead Res. to Glossop Bk.) | RIVER ETHEROW | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 135.86 | 89 | 164.75 | 4 (installed 2019) | 74.58 | Sensor failure / issue | Resolved - Nov | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0293
United Utilities | OLD ROAD CSO | Old Road CSO | 016982635 | PEA0070 | SO | SO on sewer network | SK0229097370 | GB112069060780 | Etherow (Woodhead Res. to Glossop Bk.) | SYKE CULVERT TO RIVER ETHEROW | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 13.5 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0294
United Utilities | THURSBY STW | THURSBY WwTW | 017570018 | 17570018 | SO | Inlet SO at WwTW | NY3173050340 | GB102075073410 | Wampool (Upper) | MATTY BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1791.83 | 108 | 98.3333 | 3 (installed 2020) | 79.58 | Sensor failure / issue | Resolved - Dec | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0295
United Utilities | THRELKELD PS | Threlkeld Quarry PS | 017580261 | ALL0110 | SO | Storm discharge at pumping station | NY3169024680 | GB112075070460 | Glenderamackin (Greta) | RIVER GLENDERAMACKIN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 385.95 | 86 | 80.6667 | 3 (installed 2020) | 92.83 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0296
United Utilities | GATEGILL BECK M/H CSO | Gategill Beck M/H Near River Flats CSO | 01EDE0015 | EDE0015 | SO | SO on sewer network | NY3251025320 | GB112075070460 | Glenderamackin (Greta) | GATEGILL BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 89.43 | 59 | 66.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0297
United Utilities | THREAPLAND WWTS | Threapland WwTW | 017570074 | 17570074 | ST | Storm tank at WwTW | NY1555039470 | GB112075073620 | Threapland Gill | THREAPLAND GILL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 140.23 | 49 | 38.8 | 5 (installed 2018) | 97.05 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0298
United Utilities | TEMPLE SOWERBY WWTW | TEMPLE SOWERBY WwTW | 017670042 | 17670042 | SO | Inlet SO at WwTW | NY6106027880 | GB102076070950 | Crowdundle Beck - Lower | BIRK SYKE | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1108.5 | 181 | 212.25 | 4 (installed 2019) | 99.9 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0299
United Utilities | CHAPEL ST (TEMPLE SOWERBY) CSO | Chapel Street (Temple Sowerby) CSO | 01EDE0013 | EDE0013 | SO | SO on sewer network | NY6175027321 | GB102076070950 | Crowdundle Beck - Lower | BIRK SIKE | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 50 | 38 | 38 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0300
United Utilities | TEBAY STW | TEBAY WwTW | 017270018 | 17270018 | SO | Inlet SO at WwTW | NY6135202882 | GB112072071720 | Lune - conf Birk Beck to conf Rawthey | RIVER LUNE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1431.27 | 146 | 152 | 3 (installed 2020) | 99.99 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0301
United Utilities | TEBAY PUMPING STATION | Tebay Sewage PS | 017280240 | EDE0079 | SO | Storm discharge at pumping station | NY6155005240 | GB112072071760 | Lune - headwaters to conf Birk Beck | RIVER LUNE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2279.7 | 124 | 99.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0302
United Utilities | GALLOPER POOL PS | Galloper Pool PS | 017680341 | EDE0093 | SO | Storm discharge at pumping station | NY6150004601 | GB112072071720 | Lune - conf Birk Beck to conf Rawthey | GALLOPER POOL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2275.13 | 166 | 100.25 | 4 (installed 2019) | 46.86 | Telemetry or data archiving failure / issue | Resolved - Sep | Data collection - EDM non-representative location | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0303
United Utilities | SSO ADJ CROSS KEYS INN | Adjacent Cross Keys Inn | 017280324 | EDE0104 | SO | SO on sewer network | NY6164004390 | GB112072071720 | Lune - conf Birk Beck to conf Rawthey | TRIB RIVER LUNE | N/A | N/A | Not Applicable | Dec 2023 | 1201.77 | 155 |  | <1 yr (installed 2023) | 86.7021 | Installation set-up/design issue | N/A - Ongoing investigation | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0304
United Utilities | TARVIN STW | TARVIN WwTW | 016810035 | 16810035 | SO | Inlet SO at WwTW | SJ4890067500 | GB112068060290 | Milton Brook | MILTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 196.3 | 37 | 9.25 | 4 (installed 2019) | 97.08 | [5 empty] | UUG0305
United Utilities | TARPORLEY WWTW | TARPORLEY WwTW | 016810110 | 16810110 | SO | Inlet SO at WwTW | SJ5633061240 | GB112068055440 | Wettenhall Brook | WETTENHALL BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 22.42 | 14 | 35.6 | 5 (installed 2018) | 100 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG0306
United Utilities | TARPORLEY WWTW | TARPORLEY WwTW | 016810110 | 16810110 | ST | Storm tank at WwTW | SJ5633061240 | GB112068055440 | Wettenhall Brook | WETTENHALL BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 292.17 | 87 | 92.4 | 5 (installed 2018) | 93.36 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0307
United Utilities | TALKIN WWTW | TALKIN WwTW | 017670095 | 17670095 | ST | Storm tank at WwTW | NY5475057700 | GB102076074040 | Gelt | WILLY BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 154.39 | 52 | 44.25 | 4 (installed 2019) | 99.81 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0308
United Utilities | STRINES STW | STRINES WwTW | 016940182 | 16940182 | SO | Inlet SO at WwTW | SJ9701187101 | GB112069060960 | Goyt (Sett to Etherow) | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 12 | 4 (installed 2019) | 100 | [5 empty] | UUG0309
United Utilities | STRINES STW | STRINES WwTW | 016940182 | 16940182 | ST | Storm tank at WwTW | SJ9701187101 | GB112069060960 | Goyt (Sett to Etherow) | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 954.52 | 108 | 96.25 | 4 (installed 2019) | 91.85 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0310
United Utilities | STRETFORD WWTW | STRETFORD WwTW | 016940152 | 16940152 | ST | Storm tank at WwTW | SJ7806093180 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 220.25 | 29 | 66.25 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0311
United Utilities | BRADLEY LANE (SRETFORD) CSO | Bradley Lane (Stretford) CSO | 016982547 | TRA0036 | SO | SO on sewer network | SJ7787093460 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 659 | 85 | 68.6667 | 3 (installed 2020) | 62.97 | Sensor failure / issue | Resolved - Oct | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0312
United Utilities | PARK ROAD (STRETFORD) CSO | Park Road (Stretford) CSO | EPRSB3398RR | TRA0047 | SO | SO on sewer network | SJ7088091510 | GB112069061011 | Mersey/ Manchester Ship Canal (Irwell/Manchester Ship Canal to B | BENT LANE BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1.9 | 3 | 2.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG0313
United Utilities | SOUTH OF PEEL TERRACE CSO | South of Peel Terrace CSO | 01TRA0051 | TRA0051 | SO | SO on sewer network | SJ7945093410 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIV. MERSEY/KICKETY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0314
United Utilities | SOUTH OF PEEL TERRACE CSO | South of Peel Terrace, Chester Road, MHT (Outlet 2) | 01TRA0052 | TRA0052 | SO | SO on sewer network | SJ7945093410 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | River Mersey | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0315
United Utilities | WALWYN CLOSE CSO 45049 | Walwyn Close CSO | 01TRA0056 | TRA0056 | SO | SO on sewer network | SJ8009093550 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 232.68 | 103 | 78 | 6 (installed 2017) | 92.32 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0316
United Utilities | CASTLETON AVENUE CSO 451IU | Castleton Avenue CSO | 016940192 | TRA0065 | SO | SO on sewer network | SJ7878095380 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | LONGFORD BROOK TRIB SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.6 | 4 | 13.6 | 5 (installed 2018) | 100 | [5 empty] | UUG0317
United Utilities | LOSTOCK GROVE CSO | Lostock Grove CSO | 016940193 | TRA0066 | SO | SO on sewer network | SJ7884095310 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | LONGFORD BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1.33 | 2 | 1.6667 | 3 (installed 2020) | 99.99 | [5 empty] | UUG0318
United Utilities | CROMFORD AVENUE CSO 451P7 | Cromford Avenue CSO | 016940200 | TRA0067 | SO | SO on sewer network | SJ7879095370 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | LONGFORD BROOK TRIB SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 156.23 | 15 | 3.6 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0319
United Utilities | BRADWELL AVENUE CSO | Bradwell Avenue CSO (451HA) (TRA0068) | 016940228 | TRA0068 | SO | SO on sewer network | SJ7854095610 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | LONGFORD BROOK TRIB SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.6 | 5 | 14.8 | 5 (installed 2018) | 100 | [5 empty] | UUG0320
United Utilities | DAVYHULME ROAD EAST | Davyhulme Road East | 016982694 | TRA0081 | SO | SO on sewer network | SJ8003094950 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | LONGFORD BROOK | N/A | N/A | Not Applicable | Dec 2023 | 0.17 | 1 |  | <1 yr (installed 2023) | 94.7059 | [5 empty] | UUG0321
United Utilities | 329 BARTON ROAD CSO | Barton Road CSO | 016892359 | TRA0103 | SO | SO on sewer network | SJ7886095300 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | BENT LANES BROOK/LONGFORD BROO | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 14.23 | 28 | 44 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0322
United Utilities | STONETHWAITE WWTW | STONETHWAITE WwTW | 017570056 | 17570056 | ST | Storm tank at WwTW | NY2594014160 | GB112075070340 | Stonethwaite Beck | TRIB STONETHWAITE BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 403.39 | 46 | 47.6 | 5 (installed 2018) | 99.95 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0323
United Utilities | STOCKPORT WWTW | STOCKPORT WwTW | 016940151 | 16940151 | SO | Inlet SO at WwTW | SJ8652089820 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 567.9 | 102 | 80.8571 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0324
United Utilities | STOCKPORT WWTW | STOCKPORT WwTW | 016940151 | 16940151 | ST | Storm tank at WwTW | SJ8652089820 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 451.5 | 67 | 131.4286 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0325
United Utilities | 242 STOCKPORT RD WEST | 242 Stockport Road West CSO | 01STK0002 | STK0002 | SO | SO on sewer network | SJ9202091751 | GB112069061000 | Goyt (Etherow to Mersey) | CROOKILLEY BROOK CULVERT | N/A | N/A | Not Applicable | Dec 2023 | 0 | 0 |  | <1 yr (installed 2023) | 96.3235 | [5 empty] | UUG0326
United Utilities | STOCKPORT RD WEST/ASHTON RD CSO | Stockport Road West/Ashton Road CSO | NPSWQD010908 | STK0003 | SO | SO on sewer network | SJ9182091700 | GB112069061000 | Goyt (Etherow to Mersey) | CROOKILLEY BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 5.3333 | 3 (installed 2020) | 24.03 | Comms failure / issue | Resolved - January after reporting year |  |  |  | UUG0327
United Utilities | OTTERSPOOL ROAD CSO | Otterspool Road Combined Sewer Overflow | 016993555 | STK0005 | SO | SO on sewer network | SJ9365089600 | GB112069061000 | Goyt (Etherow to Mersey) | THE RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1495.97 | 165 | 151 | 3 (installed 2020) | 70.97 | Sensor failure / issue | Resolved - Aug | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0328
United Utilities | HIGHER BENTS LANE/NEWLYN DR CSO | Higher Bents Lane/Newlyn Road CSO | 01STK0008 | STK0008 | SO | SO on sewer network | SJ9236091120 | GB112069061000 | Goyt (Etherow to Mersey) | BREDBURY STREAM VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 2.4 | 8 | 8.6667 | 3 (installed 2020) | 95.74 | [5 empty] | UUG0329
United Utilities | HURSTHEADS LANE/GREEN LANE CSO | Hurstheads Lane/Green Lane CSO | NPSWQD010893 | STK0009 | SO | SO on sewer network | SJ9356090430 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 364.06 | 104 | 87.3333 | 3 (installed 2020) | 96.69 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0330
United Utilities | BREDBURY UID CSO TANK | BREDBURY UID CSO | NPSWQD010894 | STK0011 | SO | SO on sewer network | SJ9208991712 | GB112069061000 | Goyt (Etherow to Mersey) | CROOKILLEY BROOK VIA A SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2.33 | 3 | 5 | 4 (installed 2019) | 99.81 | [5 empty] | UUG0331
United Utilities | STOCKPORT ROAD WEST CSO | Stockport Road West CSO | 01STK0012 | STK0012 | SO | SO on sewer network | SJ9102091120 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.33 | 2 | 1 | 3 (installed 2020) | 100 | [5 empty] | UUG0332
United Utilities | BRINNINGTON RISE CSO 431GD | Brinnington Rise CSO | 016940358 | STK0038 | SO | SO on sewer network | SJ9064091850 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 4.23 | 8 | 8.6 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0333
United Utilities | GREAT UNDERBANK CSO 43200 STK0039 | Great Underbank CSO | 016940449 | STK0039 | SO | SO on sewer network | SJ8947090460 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | CLVRT SECTION OF RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 30 | 29 | 40.1667 | 6 (installed 2017) | 76.45 | Sensor failure / issue | Resolved - Nov | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0334
United Utilities | MANOR ROAD PUMPING STATION | Manor Road PS | 016942050 | STK0042 | SO | Storm discharge at pumping station | SJ9366092450 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 6.23 | 10 | 16.2 | 5 (installed 2018) | 99.78 | [5 empty] | UUG0335
United Utilities | STOCKPORT RD ESSEX AVE CSO 432SK | Stockport Road/Essex Avenue CSO | 016982653 | STK0053 | SO | SO on sewer network | SJ8776089891 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY ESTUARY VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 26.73 | 35 | 54.8333 | 6 (installed 2017) | 61.56 | Comms failure / issue | Resolved - January after reporting year | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0336
United Utilities | PENNY LANE GRIMESBOTTOM CSO 43122 | Penny Lane (Grimesbottom) CSO | 016982654 | STK0081 | SO | SO on sewer network | SJ8975091240 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 439.16 | 66 | 54.6 | 5 (installed 2018) | 58.07 | Sensor failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0337
United Utilities | NEWBRIDGE LANE CSO | Newbridge Lane CSO | 016982656 | STK0086 | SO | SO on sewer network | SJ9039090710 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 100 | [5 empty] | UUG0338
United Utilities | NEWBRIDGE LANE CSO | Newbridge Lane CSO | 016982657 | STK0087 | SO | SO on sewer network | SJ9039090710 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 26.9 | 6 | 5.3333 | 3 (installed 2020) | 97.05 | [5 empty] | UUG0339
United Utilities | NEWBRIDGE LN CROMER ST CSO 432HT | Newbridge Lane / Cromer Street CSO | 016982658 | STK0088 | SO | SO on sewer network | SJ9046090780 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.17 | 2 | 1 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0340
United Utilities | JUNC STRINGER ST/NEW BRIDGE LN CSO | Stringer Street/Newbridge Lane CSO | 01STK0089 | STK0089 | SO | SO on sewer network | SJ9039090700 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 1 | 3 (installed 2020) | 100 | [5 empty] | UUG0341
United Utilities | LANCASTER STREET CSO 432CD | Lancaster Street CSO | 016982666 | STK0101 | SO | SO on sewer network | SJ9029090670 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.2 | 1 | 3.2 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0342
United Utilities | 95/97 CRAIG ROAD HEATON MERSEY CSO | 95/97 Craig Road CSO | 016982667 | STK0102 | SO | SO on sewer network | SJ8726089930 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 1.73 | 6 | 19.1667 | 6 (installed 2017) | 100 | [5 empty] | UUG0343
United Utilities | THE CIRCUIT CSO 432UT | The Circuit CSO | 016982668 | STK0103 | SO | SO on sewer network | SJ8748089890 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 78.23 | 68 | 45 | 6 (installed 2017) | 96.95 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0344
United Utilities | WELLINGTON ROAD SOUTH CSO | Wellington Road South CSO | 016982671 | STK0106 | SO | SO on sewer network | SJ8930190321 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 186.65 | 86 | 73.4286 | 7 (installed 2016) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0345
United Utilities | Hope Street CSO | Hope Street CSO | 16982763 | STK0107 | SO | SO on sewer network | SJ8876090270 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | River Mersey | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 309.19 | 118 | 105.4286 | 7 (installed 2016) | 99.85 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0346
United Utilities | PRINCES STREET CSO | Prince's Street CSO | 016982672 | STK0108 | SO | SO on sewer network | SJ8948090590 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 42.97 | 73 | 73.2857 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP or Green Recovery | UUG0347
United Utilities | AVENUE ST BREWERY ST CSO | Avenue Street/Brewery Street CSO | 016982673 | STK0109 | SO | SO on sewer network | SJ8985090870 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 18.57 | 23 | 25.8 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0348
United Utilities | CHESTERGATE CSO 431A3 | Chestergate CSO | 01STK0110 | STK0110 | SO | SO on sewer network | SJ8926090300 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 6.27 | 5 | 13.1667 | 6 (installed 2017) | 100 | [5 empty] | UUG0349
United Utilities | CHESTERGATE/KING STREET WEST CSO | Chestergate/King Street West CSO | 016982674 | STK0111 | SO | SO on sewer network | SJ8899090260 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0.57 | 3 | 34.8333 | 6 (installed 2017) | 100 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG0350
United Utilities | BRINKSWAY BRIDGE/GVILLE STREET CSO | Brinksway Bridge/Grenville Street CSO | 016982764 | STK0113 | SO | SO on sewer network | SJ8850090020 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0.2 | 2 | 5.8333 | 6 (installed 2017) | 100 | [5 empty] | UUG0351
United Utilities | 103 BRINKSWAY/LARK HILL | 103 Brinksway/Lark Hill CSO | 016982676 | STK0114 | SO | SO on sewer network | SJ8845089970 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Dec 2023 | 0 | 0 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0352
United Utilities | TRAVIS BROW/GEORGES ROAD CSO | Travis Brow/Georges Road CSO | 016982677 | STK0115 | SO | SO on sewer network | SJ8860090210 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 213.55 | 110 | 84.1429 | 7 (installed 2016) | 99.25 |  |  | Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0353
United Utilities | BRIGHTON ROAD CSO | Brighton Road CSO | 016982678 | STK0116 | SO | SO on sewer network | SJ8811089990 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 31 | 51 | 87.2857 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0354
United Utilities | WELLINGTON RD NORTH/ | Wellington Road North / Crossley Road CSO | 016982765 | STK0117 | SO | SO on sewer network | SJ8785093180 | GB112071065270 | Darwen - conf Davy Field Bk to conf Blakewater | RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1937.44 | 162 | 68.2 | 5 (installed 2018) | 30.68 | Sensor failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0355
United Utilities | HEATON MOOR CSO 431YX | Heaton Moor CSO | 016982679 | STK0119 | SO | SO on sewer network | SJ8596090050 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 25.1 | 27 | 9.3333 | 6 (installed 2017) | 100 | [5 empty] | UUG0356
United Utilities | COMPSTALL ROAD ROMILY CSO | Compstall Road (Romilly)CSO | 016982770 | STK0131 | SO | SO on sewer network | SJ9409089830 | GB112069061050 | Etherow (Glossop Brook to Goyt) | RIVER GOYT VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 184.95 | 85 | 77.75 | 4 (installed 2019) | 91.16 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0357
United Utilities | CARRINGTON RD/OFFERTON ST | Carrington Road/Offerton Street CSO | 016982686 | STK0132 | SO | SO on sewer network | SJ9067090960 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | Not Applicable | Dec 2023 | 0.7 | 16 |  | <1 yr (installed 2023) | 97.4747 | [5 empty] | UUG0358
United Utilities | JUNC STRINGER ST/NEW BRIDGE LN CSO | Junction Stringer Street/New Bridge Lane CSO | 016892181 | STK0145 | SO | SO on sewer network | SJ9039090700 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.1 | 2 | 1.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0359
United Utilities | STAVELEY WWTW | STAVELEY WwTW | 017370061 | 17370061 | SO | Inlet SO at WwTW | SD4827098020 | GB112073071380 | Kent - conf Gowan to conf Sprint | RIVER KENT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 490.62 | 40 | 66 | 5 (installed 2018) | 98.53 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0360
United Utilities | STAVELEY WWTW | STAVELEY WwTW | 017370061 | 17370061 | ST | Storm tank at WwTW | SD4827098020 | GB112073071380 | Kent - conf Gowan to conf Sprint | RIVER KENT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 4846.11 | 283 | 290.6 | 5 (installed 2018) | 99.77 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0361
United Utilities | ST HELENS STW | St Helens Wastewater Treatment Works (Site STHEL) (016920130) | 016920130 | 16920130 | SO | Inlet SO at WwTW | SJ5358095920 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | SANKEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 112.31 | 39 | 37 | 3 (installed 2020) | 100 | [5 empty] | UUG0362
United Utilities | ST HELENS STW | St Helens Wastewater Treatment Works (Site STHEL) (016920130) | 016920130 | 16920130 | ST | Storm tank at WwTW | SJ5358095920 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | SANKEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1237.19 | 93 | 90.6667 | 3 (installed 2020) | 98.91 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0363
United Utilities | SANKEY BROOK (ST HELENS) CSO | Sankey Brook (St Helens) CSO | NPSWQD010822 | STH0005 | SO | SO on sewer network | SJ5153096240 | GB112069061240 | Rainford Brook | RAINFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 116.43 | 32 | 28 | 4 (installed 2019) | 99.7 | [5 empty] | UUG0364
United Utilities | MALVERN ROAD CSO (42052) | Malvern Road (St.Helens) CSO | 016982535 | STH0013 | SO | SO on sewer network | SJ5408095850 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | SANKEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 84.68 | 54 | 53 | 3 (installed 2020) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0365
United Utilities | WARRINGTON NEW ROAD (42060) | Warrington New Road CSO | 016993695 | STH0050 | SO | SO on sewer network | SJ5187095180 | GB112069061210 | Hardshaw (Windle) Brook | HARDSHAW BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 52.25 | 31 | 24.3333 | 3 (installed 2020) | 87.13 | Comms failure / issue | Resolved - Apr |  |  |  | UUG0366
United Utilities | HARESFINCH ROAD | Haresfinch Road CSO | 01STH0051 | STH0051 | SO | SO on sewer network | SJ5162096220 | GB112069061240 | Rainford Brook | RAINFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2021 - full year data expected | 130.43 | 58 | 29 | 2 (installed 2021) | 99.99 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0367
United Utilities | WARRINGTON NEW ROAD CSO | Warrington New Road CSO | 01STH0052 | STH0052 | SO | SO on sewer network | SJ5195095050 | GB112069061210 | Hardshaw (Windle) Brook | HARDSHAW BROOK | N/A | N/A | Not Applicable | Dec 2023 | 1.37 | 4 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0368
United Utilities | JACKSON STREET CSO | Jackson Street CSO | EPRQB3594RZ | STH0053 | SO | SO on sewer network | SJ5220094960 | GB112069061210 | Hardshaw (Windle) Brook | HARDSHAW BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 28.32 | 23 | 23.5 | 4 (installed 2019) | 90.49 | [5 empty] | UUG0369
United Utilities | GLOUCESTER STREET | Gloucester Street CSO | 01STH0054 | STH0054 | SO | SO on sewer network | SJ5246094970 | GB112069061180 | Sankey Brook (Hardshaw Brook to Rainford Brook | SANKEY BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0370
United Utilities | GASKELL STREET CSO | Gaskell Street CSO | 016982533 | STH0056 | SO | SO on sewer network | SJ5255094630 | GB112069061170 | Sutton Brook | SUTTON BROOK TRIB SANKEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 56.75 | 50 | 59.8 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP or Green Recovery | UUG0371
United Utilities | WASHWAY LANE | Washway Lane CSO | 016920387 | STH0058 | SO | SO on sewer network | SJ5134097130 | GB112069061240 | Rainford Brook | RAINFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 295.06 | 72 | 56.75 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0372
United Utilities | CARR MILL ROAD CSO | Carr Mill Road CSO | 016982538 | STH0059 | SO | SO on sewer network | SJ5290097558 | GB112069061230 | Black Brook (Mersey Estuary) | BLACK BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 151.93 | 84 | 78.25 | 4 (installed 2019) | 96.72 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0373
United Utilities | BERRYS LANE COMBINED SEWER OVERFLOW | Berrys Lane | 016982532 | STH0060 | SO | SO on sewer network | SJ5347094380 | GB112069061170 | Sutton Brook | SUTTON BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 40.77 | 17 | 15 | 4 (installed 2019) | 97.23 | [5 empty] | UUG0374
United Utilities | DOCK ST OVERFLOW | Dock Street CSO | 01WYR0028 | WYR0028 | SO | SO on sewer network | SD3389047630 | 341 |  | COPSE BROOK CULVERT | N/A | N/A | Not Applicable | Dec 2023 | 29 | 39 |  | <1 yr (installed 2023) | 97.18 | [5 empty] | UUG0375
United Utilities | FOLDS ROAD COMBINED SEWER OVERFLOW | Folds Road CSO | 016993696 | STH0064 | SO | SO on sewer network | SJ5372096100 | GB112069061230 | Black Brook (Mersey Estuary) | BLACK BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 346.79 | 107 | 100.5 | 4 (installed 2019) | 90.32 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0376
United Utilities | MILL LANE PS | XX Mill Lane (St.Helens) CSO | 016990476 | STH0065 | SO | SO on sewer network | SJ9050093500 | GB112069061112 | Sutton Brook | Sutton Mill Brook via Surface water sewer | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2.03 | 6 | 2.5 | 4 (installed 2019) | 97.59 | [5 empty] | UUG0377
United Utilities | RUDD AVENUE | Rudd Avenue SSO | 016982534 | STH0066 | SO | SO on sewer network | SJ5467094920 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | SANKEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 86.85 | 48 | 54 | 3 (installed 2020) | 99.39 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0378
United Utilities | ST HELENS ROAD CSO 422SZ | St Helens Road CSO | 016982537 | STH0067 | SO | SO on sewer network | SJ4852093690 | GB112069061210 | Hardshaw (Windle) Brook | UNNAMED TRIB OF ECCLESTON MERE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 28.73 | 48 | 71.8 | 5 (installed 2018) | 92.61 |  |  | Data collection - EDM non-representative location | Resolved - Jun | Other investigation - non-WINEP/Green Recovery | UUG0379
United Utilities | GRANGE VALLEY | Grange Valley | 01STH0069 | STH0069 | SO | Storm discharge at pumping station | SJ5585096140 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | FRESHWATER STTEAM | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.2 | 1 | 8.5 | 4 (installed 2019) | 100 | [5 empty] | UUG0380
United Utilities | CRAB ST/DUKE ST | Cooper Street | 01STH0073 | STH0073 | SO | SO on sewer network | SJ5075095760 | GB112069061210 | Hardshaw (Windle) Brook | Hardshaw Brook | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0381
United Utilities | VICARAGE ROAD | Vicarage Road CSO | 01STH0079 | STH0079 | SO | SO on sewer network | SJ5429097180 | GB112069061230 | Black Brook (Mersey Estuary) | Clipsley Brook | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 19.53 | 5 | 4.2 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0382
United Utilities | LEACH LANE ST HELENS CSO | Leach Lane (St. Helens) CSO | 016982980 | STH0112 | SO | SO on sewer network | SJ5265092360 | GB112069061170 | Sutton Brook | SUTTON MILL BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 7.2 | 21 | 26.75 | 4 (installed 2019) | 100 | [5 empty] | UUG0383
United Utilities | SPARK BRIDGE PUMPING STATION | Spark Bridge Wastewater Network Pumping Station | EPRBP3624XL | LAK0108 | SO | Storm discharge at pumping station | SD3068084701 | GB112073071190 | Crake | RIVER CRAKE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 2751.52 | 153 | 115.3333 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0384
United Utilities | SOUTHWAITE WWTW | SOUTHWAITE WwTW | 017670112 | 17670112 | SO | Inlet SO at WwTW | NY4495046350 | GB102076074030 | Petteril d/s Blackrack Beck | RIVER PETTERIL | N/A | N/A | Not Applicable | Commissioned pre-2016 - full year data expected | 8.79 | 2 | 0.25 | 8 (installed 2015) | 100 | [5 empty] | UUG0385
United Utilities | SOUTHWAITE PS | Southwaite PS | 017680340 | EDE0091 | SO | Storm discharge at pumping station | NY4499045170 | GB102076074030 | Petteril d/s Blackrack Beck | TRIB RIVER PETTERIL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 42.93 | 16 | 10.75 | 4 (installed 2019) | 99.79 | [5 empty] | UUG0386
United Utilities | CHILTERN AVENUE CSO | Chiltern Avenue CSO | 017280299 | WYR0062 | SO | SO on sewer network | SD3414039350 | 180 |  | HORSE BRIDGE DYKE | N/A | Fleetwood | Not Applicable | Commissioned in 2016 - full year data expected | 0.93 | 5 | 3.4286 | 7 (installed 2016) | 97.9 | [5 empty] | UUG0387
United Utilities | BALMORAL DRIVE/NORTH ROAD CSO | Balmoral Drive/North Road CSO | 01SEF0008 | SEF0008 | SO | SO on sewer network | SD3715019591 | GB112070064830 | Three Pool's Waterway | RIVER RIBBLE | N/A | Southport | Not Applicable | Commissioned in 2016 - full year data expected | 16.07 | 10 | 39 | 7 (installed 2016) | 100 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG0388
United Utilities | OPPOSITE NO. 320 LIVERPOOL ROAD CSO | Opposite No.320 Liverpool Road CSO | 01SEF0053 | SEF0053 | SO | SO on sewer network | SD3319013610 | GB112070064830 | Three Pool's Waterway | SANDY BROOK (TRIB. RIVER ALT) | N/A | St Annes, St Annes North, Blackpool South, Blackpool Central, Blackpool North, Southport, Ainsdale | Not Applicable | Commissioned in 2016 - full year data expected | 7.6 | 4 | 6.8571 | 7 (installed 2016) | 100 | [5 empty] | UUG0389
United Utilities | OPPOSITE NO.36 CARR LANE CSO | Opposite 36 Carr Lane CSO | 01SEF0054 | SEF0054 | SO | SO on sewer network | SD3302013221 | GB112070064830 | Three Pool's Waterway | SANDY BROOK (TRIB. RIVER ALT) | N/A | St Annes, St Annes North, Blackpool South, Blackpool Central, Blackpool North, Southport, Ainsdale | Not Applicable | Commissioned in 2016 - full year data expected | 27.73 | 20 | 24 | 7 (installed 2016) | 99.17 | [5 empty] | UUG0390
United Utilities | REAR NO.1 HASTINGS ROAD CSO 381P8 | Rear No.1 Hastings Road CSO | 01SEF0055 | SEF0055 | SO | SO on sewer network | SD3302013223 | GB112070064830 | Three Pool's Waterway | SANDY BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 4.83 | 9 | 6.1667 | 6 (installed 2017) | 100 | [5 empty] | UUG0391
United Utilities | OPPOSITE NO 7 CROMER ROAD CSO | Opposite No.7 Cromer Road CSO | 01SEF0056 | SEF0056 | SO | SO on sewer network | SD3302013222 | GB112070064830 | Three Pool's Waterway | TRIB SANDY BROOK | N/A | St Annes, St Annes North, Blackpool South, Blackpool Central, Blackpool North, Southport, Ainsdale | Not Applicable | Commissioned in 2017 - full year data expected | 3 | 6 | 7 | 6 (installed 2017) | 99.06 | [5 empty] | UUG0392
United Utilities | O/S 65 DOVER ROAD CSO 381P8 | O/s 65 Dover Road CSO | 01SEF0057 | SEF0057 | SO | SO on sewer network | SD3302013220 | GB112070064830 | Three Pool's Waterway | SANDY BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 8.9 | 9 | 6.8333 | 6 (installed 2017) | 100 | [5 empty] | UUG0393
United Utilities | WEST ROAD CSO 38055 | Weld Road CSO | 01SEF0064 | SEF0064 | SO | SO on sewer network | SD3171016030 | GB641211630001 | Mersey Mouth | IRISH SEA | N/A | Ainsdale; Southport | Not Applicable | Commissioned in 2017 - full year data expected | 57.73 | 12 | 6.8333 | 6 (installed 2017) | 91.67 | [5 empty] | UUG0394
United Utilities | CROWLANDS STREET PUMPING STATION | Crowland Street PS | 016931043 | SEF0067 | SO | Storm discharge at pumping station | SD3671016650 | GB112070064830 | Three Pool's Waterway | THREE POOLS WATERWAY | N/A | Southport | Not Applicable | Commissioned in 2016 - full year data expected | 25.58 | 32 | 63.8571 | 7 (installed 2016) | 98.62 |  |  | Performance - Asset power failure | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0395
United Utilities | OUTS119 RUFFORD RD CSO 382PZ | O/S 119 Rufford Road CSO | 017081260 | SEF0092 | SO | SO on sewer network | SD3765019790 | GB112070064830 | Three Pool's Waterway | THREE POOLS WATERWAY | N/A | Southport | Not Applicable | Commissioned in 2017 - full year data expected | 82.8 | 44 | 56.3333 | 6 (installed 2017) | 99.73 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0396
United Utilities | JANES BROOK ROAD PUMPING STATION | Janes Brook Road PS | 01SEF0068 | SEF0068 | SO | Storm discharge at pumping station | SD3573015750 | GB112070064830 | Three Pool's Waterway | FINE JANE'S BROOK | N/A | Southport | Not Applicable | Commissioned in 2016 - full year data expected | 0.04 | 3 | 9.7143 | 7 (installed 2016) | 99.96 | [5 empty] | UUG0397
United Utilities | SKIPPOOL PUMPING STATION | Skippool Pumping Station (Site ID 52560) (WYR0076) | 017260059 | WYR0076 | SO | Storm discharge at pumping station | SD3582040850 | 180 |  | WYRE ESTUARY | N/A | Fleetwood | Not Applicable | Commissioned in 2017 - full year data expected | 1015.86 | 85 | 59.3333 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0398
United Utilities | RAVENSWOOD CSO 52568 | Ravenswood Drive CSO | 017290504 | WYR0079 | SO | SO on sewer network | SD3371037610 | 180 |  | HORSEBRIDGE DYKE | N/A | Fleetwood | Not Applicable | Commissioned in 2017 - full year data expected | 326.21 | 56 | 21 | 6 (installed 2017) | 99.04 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0399
United Utilities | SOCKBRIDGE AND TIRRIL WWTW SOCKB | SOCKBRIDGE & TIRRIL WwTW | 017670087 | 17670087 | SO | Inlet SO at WwTW | NY5014027080 | GB102076071020 | Eamont (Upper) | LADY BECK TRIB RIVER EAMONT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 142.84 | 42 | 47.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0400
United Utilities | LADY BECK CSO (172CN) | Lady Beck CSO | 01EDE0005 | EDE0005 | SO | SO on sewer network | NY5012026861 | GB102076071020 | Eamont (Upper) | LADY BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 100 | [5 empty] | UUG0401
United Utilities | SLAIDBURN WWTW | SLAIDBURN WwTW | 017160046 | 17160046 | SO | Inlet SO at WwTW | SD7090051410 | GB112071065350 | Hodder - conf Croasdale Bk to conf Easington Bk | RIVER HODDER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 49.5 | 27 | 38.2 | 5 (installed 2018) | 99.97 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG0402
United Utilities | SLAIDBURN WW NTWK PUMPING STATION | Slaidburn PS | 01RIB0003 | RIB0003 | SO | Storm discharge at pumping station | SD7131052270 | GB112071065350 | Hodder - conf Croasdale Bk to conf Easington Bk | RIVER HODDER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 20.77 | 11 | 8.3333 | 3 (installed 2020) | 99.98 | [5 empty] | UUG0403
United Utilities | SKELTON STW | SKELTON WwTW | 017670116 | 17670116 | SO | Inlet SO at WwTW | NY4345036380 | GB102076073760 | Ive | TRIB GRISE BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 551.27 | 98 | 87.3333 | 3 (installed 2020) | 99.98 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0404
United Utilities | SKELTON PS | Skelton PS | 017680339 | EDE0090 | SO | Storm discharge at pumping station | NY4327035420 | GB102076073760 | Ive | TRIB GRISE BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 147.1 | 47 | 35.75 | 4 (installed 2019) | 99.94 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0405
United Utilities | SKELMERSDALE WWTW SKELM | SKELMERSDALE WwTW | 017020107 | 17020107 | SO | Inlet SO at WwTW | SD4817412024 | GB112070064820 | Douglas - Lower | RIVER DOUGLAS | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 117.98 | 44 | 24.7143 | 7 (installed 2016) | 99.98 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0406
United Utilities | SKELMERSDALE WWTW SKELM | SKELMERSDALE WwTW | 017020107 | 17020107 | ST | Storm tank at WwTW | SD4817412024 | GB112070064820 | Douglas - Lower | RIVER DOUGLAS | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 30.5 | 11 | 39.1429 | 7 (installed 2016) | 99.74 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG0407
United Utilities | NEAR TAWD VALE INN CSO | Near Tawd Vale Inn | EPRSB3399WS | WLN0027 | SO | SO on sewer network | SD4810006990 | GB112070064790 | Tawd | RIVER TAWD VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 40.67 | 49 | 42.6667 | 3 (installed 2020) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0408
United Utilities | 194 ORMSKIRK ROAD CSO | 194 Ormskirk Road | 017081269 | WLN0048 | SO | SO on sewer network | SD4875205989 | GB112070064790 | Tawd | RIVER TAWD VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 169.87 | 73 | 68.5 | 4 (installed 2019) | 91.5 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0409
United Utilities | NR FIRE STN ORMSKIRK RD | Ormskirk Road , Skelmersdale | 017081270 | WLN0049 | SO | SO on sewer network | SD4875005890 | GB112070064790 | Tawd | RIVER TAWD | N/A | N/A | Not Applicable | Dec 2023 | 353.47 | 146 |  | <1 yr (installed 2023) | 97.3568 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0410
United Utilities | O/S 1 TEVERSHAM CSO | Outside 1 Teversham | 017081271 | WLN0050 | SO | SO on sewer network | SD4785006970 | GB112070064830 | Tawd | Pond tributary of River Tawd via surface water sewer | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 31.87 | 34 | 29.1667 | 6 (installed 2017) | 100 | [5 empty] | UUG0411
United Utilities | DOCK STREET CSO 52567 | Dock Street Combined Sewer Overflow (Site ID 52567) (WYR0080) | 017290502 | WYR0080 | SO | SO on sewer network | SD3363047580 | 341 |  | COPSE BROOK CULVERT | N/A | Fleetwood | Not Applicable | Commissioned in 2019 - full year data expected | 5.85 | 8 | 5.75 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0412
United Utilities | GLASSON WWTW | Glasson Wastewater Treatment Works (GLASN) | 017680455 | 17680455 | SO | Inlet SO at WwTW | NY2607060420 | 90 |  | TRIB SOLWAY FIRTH ESTUARINE WT | N/A | Allonby | Not Applicable | Commissioned in 2016 - full year data expected | 277.95 | 69 | 123.8571 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0413
United Utilities | GLASSON PUMPING STATION | Glasson PS | 01ALL0123 | ALL0123 | SO | Storm discharge at pumping station | NY2551060350 | 90 |  | UN-NAMED TRIB SOLWAY FIRTH | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 86.75 | 62 | 47.3333 | 6 (installed 2017) | 99.99 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0414
United Utilities | SHAP STW | SHAP WwTW | 017670025 | 17670025 | SO | Inlet SO at WwTW | NY5581015780 | GB102076070900 | Leith | SHAP BECK (RIVER LEITH) | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 943.17 | 50 | 45.25 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0415
United Utilities | SHAP PS | Shap (Brackenber) WwNPS | 017680338 | EDE0089 | SO | Storm discharge at pumping station | NY5617014270 | GB102076070690 | Lowther (Upper) | DOCKER BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1064.67 | 63 | 15.75 | 4 (installed 2019) | 99.99 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0416
United Utilities | SETTLE WASTEWATER TREATMENT WORKS | SETTLE WwTW | 017160045 | 17160045 | ST | Storm tank at WwTW | SD8080261962 | GB112071065614 | Ribble (Stainforth to Long Preston Beck) | RIVER RIBBLE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 391.25 | 54 | 90.6 | 5 (installed 2018) | 98.18 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0417
United Utilities | BRIDGE END CSO 151F5 | Bridge End CSO | 017190756 | CRA0004 | SO | SO on sewer network | SD8167564085 | GB112071065614 | Ribble (Stainforth to Long Preston Beck) | R RIBBLE VIA A SURFACE W SEWER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 3.27 | 6 | 10.6 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0418
United Utilities | PENNY BRIDGE CSO | Penny Bridge CSO | 017190752 | CRA0002 | SO | SO on sewer network | SD8145063271 | GB112071065614 | Ribble (Stainforth to Long Preston Beck) | RIVER RIBBLE | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 105.37 | 57 | 14.25 | 4 (installed 2019) | 99.73 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0419
United Utilities | GILDERSLEETS LANE CSO 151VM | Gildersleets Lane CSO | 01CRA0005 | CRA0005 | SO | SO on sewer network | SD8089062610 | GB112071065614 | Ribble (Stainforth to Long Preston Beck) | RIVER RIBBLE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 1 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0420
United Utilities | SEDBERGH STW | SEDBERGH WwTW | 017270009 | 17270009 | ST | Storm tank at WwTW | SD6512091160 | GB112072071710 | Rawthey - Lower | RIVER RAWTHEY | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1491 | 64 | 50.3333 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0421
United Utilities | SETTLEBECK SEDBERGH CSO | Settlebeck (Sedbergh) Combined Sewer Overflow | 01LAK0014 | LAK0014 | SO | SO on sewer network | SD6639091910 | GB112072071710 | Rawthey - Lower | RIVER RAWTHEY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 1.75 | 4 (installed 2019) | 96.57 | [5 empty] | UUG0422
United Utilities | MORTAR PITS COMBINED SEWER OVERFLOW | Mortar Pits CSO | 017290473 | LAK0060 | SO | SO on sewer network | SD6624091740 | GB112072071710 | Rawthey - Lower | RIVER RAWTHEY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 14.87 | 26 | 27.75 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0423
United Utilities | SEASCALE WWTW | Seascale Wastewater Treatment Works (Site ID SEASC) (017480324) | 017480324 | 17480324 | ST | Storm tank at WwTW | NY0403000930 | GB641211630002 | Cumbria | IRISH SEA | N/A | Seascale | Not Applicable | Commissioned in 2017 - full year data expected | 812.41 | 64 | 61.5 | 6 (installed 2017) | 99.73 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0424
United Utilities | SANDFORD VILLAGE WWTW | SANDFORD VILLAGE WwTW | 017680300 | 17680300 | SO | Inlet SO at WwTW | NY7306016077 | GB102076070880 | Eden - Scandal Beck to Lyvennet | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 90.8 | 34 | 80.5 | 4 (installed 2019) | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0425
United Utilities | SANDBACH WASTEWATER TREATMENT WORKS | SANDBACH WwTW | 016810106 | 16810106 | ST | Storm tank at WwTW | SJ7420059290 | GB112068055420 | Wheelock (including Hassall Brook) | RIVER WHEELOCK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 313.78 | 64 | 14 | 5 (installed 2018) | 99.99 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0426
United Utilities | MIDDLEWICH ROAD CSO 131AD | Middlewich Road CSO | 01CON0003 | CON0003 | SO | SO on sewer network | SJ7469060160 | GB112068055420 | Wheelock (including Hassall Brook) | UNNAMED TRIB RIVER WHEELOCK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 19.97 | 18 | 29 | 5 (installed 2018) | 100 | [5 empty] | UUG0427
United Utilities | BROOK MILL COMBINED SEWER OVERFLOW | Brook Mill CSO | 016881909 | CON0043 | SO | SO on sewer network | SJ7575060100 | GB112068055430 | Arclid Brook | CLVRTD SECTION OF BROOK MILL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 11.93 | 21 | 16.5 | 4 (installed 2019) | 100 | [5 empty] | UUG0428
United Utilities | CREWE ROAD MILL LANE CSO 138CG | CREWE ROAD / MILL LANE CSO | 01CON0044 | CON0044 | SO | SO on sewer network | SJ7512059070 | GB112068055420 | Wheelock (including Hassall Brook) | RIVER WHEELOCK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 1.2 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0429
United Utilities | MILL HILL LANE CSO 132F8 | MILL HILL LANE CSO | 01CON0045 | CON0045 | SO | SO on sewer network | SJ7536059830 | GB112068055430 | Arclid Brook | RIVER WHEELOCK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 10.03 | 22 | 30.8 | 5 (installed 2018) | 95.88 | [5 empty] | UUG0430
United Utilities | HASSALL ROAD CSO 131X8 | HASSALL ROAD CSO | 01CON0046 | CON0046 | SO | SO on sewer network | SJ7621059540 | GB112068055410 | Wheelock (Source to Kidsgrove Stream) | RIVER WHEELOCK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 72.7 | 36 | 34.6 | 5 (installed 2018) | 96.05 | [5 empty] | UUG0431
United Utilities | MOSS LANE SANDBACH 138CF | MOSS LANE CSO | 01CON0049 | CON0049 | SO | SO on sewer network | SJ7329060960 | GB112068055420 | Trent and Mersey Canal | TRENT AND MERSEY CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 283.5 | 41 | 133.8 | 5 (installed 2018) | 99.97 |  |  | Data collection - EDM non-representative location | Resolved - Jan | Other investigation - non-WINEP/Green Recovery | UUG0432
United Utilities | FRONT STREET CSO 13521 | FRONT STREET CSO | 01CON0047 | CON0047 | SO | SO on sewer network | SJ7611060680 | GB112068055430 | Arclid Brook | ARCLID BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 40.53 | 44 | 9.4 | 5 (installed 2018) | 99.98 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0433
United Utilities | COOKESMERE LANE | Cooksmere Lane PS | 01CON0070 | CON0070 | SO | Storm discharge at pumping station | SJ7502061790 | GB112068055460 | Croco | TRIB OF THE RIVER CROCO | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 63.43 | 21 | 17 | 5 (installed 2018) | 90.52 | [5 empty] | UUG0434
United Utilities | SALFORD WASTEWATER TREATMENT WORKS | SALFORD WwTW | 016940150 | 16940150 | SO | Inlet SO at WwTW | SJ7924097981 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 283.89 | 113 | 92.8 | 5 (installed 2018) | 100 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Scheduled | Other investigation - non-WINEP/Green Recovery | UUG0435
United Utilities | SALFORD WASTEWATER TREATMENT WORKS | SALFORD WwTW | 016940150 | 16940150 | ST | Storm tank at WwTW | SJ7924097981 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 7.2 | 5 (installed 2018) | 97.82 | [5 empty] | UUG0436
United Utilities | CROMWELL ROAD/LICHFIELD STREET CSO | CROMWELL ROAD / LICHFIELD STREET CSO | 01SAL0028 | SAL0028 | SO | SO on sewer network | SD8210000300 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2.07 | 14 | 13 | 4 (installed 2019) | 100 | [5 empty] | UUG0437
United Utilities | CLOWES ST/DANIEL ADAMSON ROAD CSO | Clowes Street/Daniel Adamson Road CSO | 016993658 | SAL0073 | SO | SO on sewer network | SJ7924097980 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 64.7 | 63 | 84.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0438
United Utilities | WELWYN DRIVE CSO 37044 | Welwyn Drive CSO | 016982967 | SAL0074 | SO | SO on sewer network | SD7823000150 | GB112069061430 | Folly Brook and Salteye Brook. | FOLLY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 46.03 | 84 | 55.4 | 5 (installed 2018) | 77.25 | Comms failure / issue | Resolved - January after reporting year | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0439
United Utilities | LANCASTER RD RADCLIFFE RD CSO 372CC | Lancaster/Radcliffe Road | 01SAL0075 | SAL0075 | SO | SO on sewer network | SJ7840099700 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | GILDA BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 83.87 | 67 | 31 | 4 (installed 2019) | 62.65 | Comms failure / issue | Resolved - January after reporting year | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0440
United Utilities | RADFORD STREET CSO | Radford Street CSO | 016993605 | SAL0079 | SO | SO on sewer network | SD8212001500 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 28.73 | 43 | 33.75 | 4 (installed 2019) | 96.15 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0441
United Utilities | VICTORIA RD/ORVIETTO AVENUE CSO | Victoria Road/Orvietto Avenue CSO | 016993481 | SAL0078 | SO | SO on sewer network | SJ7844099750 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | GILDA BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.1 | 1 | 6 | 5 (installed 2018) | 100 | [5 empty] | UUG0442
United Utilities | COTTENHAM LANE CSO 372RZ | Cottenham Lane CSO | 01SAL0081 | SAL0081 | SO | SO on sewer network | SJ8337099340 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 26.17 | 16 | 8.3333 | 6 (installed 2017) | 99.98 | [5 empty] | UUG0443
United Utilities | LAUNDRY ST/DUCHY RD CSO | Laundry Street/Duchy Road Combined Sewer Overflow | 016993761 | SAL0082 | SO | SO on sewer network | SD8153000410 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 31.67 | 43 | 46.3333 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0444
United Utilities | LANGLEY ROAD CSO | Langley Road CSO | 016993610 | SAL0092 | SO | SO on sewer network | SD8070001000 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 136.67 | 60 | 59.6667 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0445
United Utilities | GREAT CLOWES CSO 37048 SAL0080 | Great Clowes Street/Sussex Street CSO | 016993788 | SAL0080 | SO | SO on sewer network | SJ8290099370 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 80.67 | 95 | 75.3333 | 6 (installed 2017) | 98.72 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0446
United Utilities | LITTLETON ROAD CSO | Littleton Road CSO | EPRSB3396WD | SAL0112 | SO | SO on sewer network | SD8175000500 | GB112069061451 | Irwell (Croal to Irk) | THE RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 37.43 | 29 | 13.6667 | 3 (installed 2020) | 95.29 | [5 empty] | UUG0447
United Utilities | FREDERICK ROAD CSO (371UV) | Frederick Road CSO | 016940467 | SAL0140 | SO | SO on sewer network | SJ8216099790 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 42.13 | 29 | 22.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG0448
United Utilities | HANKINSON WAY CSO | Hankinson Way CSO | 016982903 | SAL0185 | SO | SO on sewer network | SJ7961097700 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 5.53 | 16 | 9.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0449
United Utilities | LANCASTER ROAD/HAYFIELD ROAD TANK | Lancaster Road/Hayfield Road Detention Tank | 016993482 | SAL0192 | SO | SO on sewer network | SJ7877099770 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | GILDA BROOK(MANC SHIP) VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 5.26 | 52 | 50.25 | 4 (installed 2019) | 90.38 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0450
United Utilities | LANGLEY RD NORTH CSO | Langley Road North CSO | 016982973 | SAL0187 | SO | SO on sewer network | SD8081001070 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0451
United Utilities | BUFFALO COURT DETENTION TANK | BUFFALO COURT DETENTION TANK (37066) | EPRDB3690DM | SAL0195 | SO | SO on sewer network | SJ8013097730 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Dec 2023 | 1722.22 | 105 |  | <1 yr (installed 2023) | 100 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0452
United Utilities | SALE WWTW (SALEZ) | SALE WwTW | 016940149 | 16940149 | SO | Inlet SO at WwTW | SJ7677092920 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | STROMFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 898.76 | 133 | 139.25 | 4 (installed 2019) | 97.83 |  |  | Data collection - EDM non-representative location | Resolved - Aug | Other investigation - non-WINEP/Green Recovery | UUG0453
United Utilities | SALE WWTW (SALEZ) | SALE WwTW | 016940149 | 16940149 | ST | Storm tank at WwTW | SJ7677092920 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | STROMFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 760.22 | 154 | 146.75 | 4 (installed 2019) | 99.75 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | resolved - dec | Other investigation - non-WINEP/Green Recovery | UUG0454
United Utilities | MANOR AVENUE/FIRS ROAD CSO | Manor Avenue/Firs Road CSO | 016892365 | TRA0006 | SO | SO on sewer network | SJ7646092840 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | STROMFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 5.03 | 7 | 10.6 | 5 (installed 2018) | 99.88 | [5 empty] | UUG0455
United Utilities | MANOR AVENUE CARRINGTON LANE CSO | Manor Avenue/Carrington Lane CSO | 016892366 | TRA0043 | SO | SO on sewer network | SJ7645092840 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | STROMFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 33.37 | 36 | 34.6 | 5 (installed 2018) | 100 | [5 empty] | UUG0456
United Utilities | MANOR AVENUE PS | Manor Avenue PS | 016983142 | TRA0049 | SO | Storm discharge at pumping station | SJ7636092850 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | STROMFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 5 | 3 | 13.6 | 5 (installed 2018) | 99.98 | [5 empty] | UUG0457
United Utilities | DANEFIELD ROAD CSO 45052 | The Danefield Road CSO | 016982773 | TRA0086 | SO | SO on sewer network | SJ7928093210 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY (UNDER M63) | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 768.87 | 49 | 17.3333 | 6 (installed 2017) | 83.26 | Sensor failure / issue | Resolved - Aug | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0458
United Utilities | MANOR AVENUE CSO (45056) | Manor Avenue CSO | 016982887 | TRA0095 | SO | SO on sewer network | SJ7645092841 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | STROMFORD BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 80.23 | 78 | 74 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0459
United Utilities | THE AVENUE SYPHON CSO 452UO | The Avenue Syphon CSO | 016982888 | TRA0096 | SO | SO on sewer network | SJ7645092842 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | STROMFORD BRK TRIB RVR MERSEY | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 57.83 | 42 | 50.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0460
United Utilities | SADDLEWORTH WWTW | SADDLEWORTH WwTW | 016940090 | 16940090 | ST | Storm tank at WwTW | SD9929004310 | GB112069064741 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2748.92 | 162 | 146 | 4 (installed 2019) | 99.94 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0461
United Utilities | DELPH NEW ROAD/STATION APPROACH CSO | Delph New Road/Station SSO | 016982525 | OLD0009 | SO | SO on sewer network | SD9873007430 | GB112069064741 | Tame (Source to Chew Brook) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 16.47 | 16 | 154 | 4 (installed 2019) | 50.66 | Comms failure / issue | Resolved - January after reporting year | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0462
United Utilities | DOBCROSS NEW ROAD CSO | Dobcross New Road CSO | 016982509 | OLD0011 | SO | SO on sewer network | SD9904006320 | GB112069064741 | Tame (Source to Chew Brook) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 699.5 | 44 | 17 | 4 (installed 2019) | 99.99 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0463
United Utilities | CLIFTON HOLMES CSO | Clifton Holmes CSO | 016982526 | OLD0014 | SO | SO on sewer network | SD9818008040 | GB112069064741 | Tame (Source to Chew Brook) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 257.67 | 86 | 77.75 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0464
United Utilities | STANDEDGE RD DIGGLE SSO | Standedge Road SSO | 016982528 | OLD0016 | SO | SO on sewer network | SD9985006900 | GB112069064741 | Tame (Source to Chew Brook) | DIGGLE BROOK | N/A | N/A | Not Applicable | Dec 2023 | 839.23 | 174 |  | <1 yr (installed 2023) | 98.01 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0465
United Utilities | GRASSCROFT SEWAGE SCHEME | Armit Road (Grasscroft) CSO | 016950639 | OLD0107 | SO | SO on sewer network | SD9802003930 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 24.07 | 9 | 16.25 | 4 (installed 2019) | 55.2 | Comms failure / issue | Resolved - January after reporting year |  |  |  | UUG0466
United Utilities | GREENFIELD CHEW VALLEY ROAD CSO | Greenfield Chew Valley Combined Sewer Overflow | 01OLD0059 | OLD0059 | SO | SO on sewer network | SD9935004350 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1372.57 | 90 | 48.5 | 4 (installed 2019) | 96.08 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0467
United Utilities | St Anne's Square | St Anne's Square | 016982634 | OLD0138 | SO | SO on sewer network | SD9861907880 | GB112069064741 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 529.4 | 98 | 98 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0468
United Utilities | MANCHESTER ROAD (GREENFIELD) CSO | Manchester Road (Greenfield) CSO | 017670081 | OLD0137 | SO | SO on sewer network | SD9886603857 | GB102076070940 | Dacre Beck (Lower) | DACRE BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0469
United Utilities | HOREST LANE COMBINED SEWER OVERFLOW | Horest Lane CSO | 016982961 | OLD0153 | SO | SO on sewer network | SD9705009250 | GB112069064741 | Tame (Source to Chew Brook) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 1 | 4 (installed 2019) | 100 | [5 empty] | UUG0470
United Utilities | EAST GREENFIELD CSO | East Greenfield CSO | 016982923 | OLD0152 | SO | SO on sewer network | SD9929004290 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0.75 | 4 (installed 2019) | 100 | [5 empty] | UUG0471
United Utilities | RUSHTON WASTEWATER TREATMENT WORKS | RUSHTON WwTW | 016810105 | 16810105 | ST | Storm tank at WwTW | SJ5781063180 | GB112068055440 | Wettenhall Brook | TRIB WETTENHALL BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 89.5 | 6 | 17.2 | 5 (installed 2018) | 99.69 | [5 empty] | UUG0472
United Utilities | RUNCORN WASTEWATER TREATMENT WORKS | RUNCORN WwTW | 016820127 | 16820127 | ST | Storm tank at WwTW | SJ5412083830 | GB531206908100 | Manchester Ship Canal | M/C SHIP CANAL (TIDAL) | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 883.13 | 69 | 37.2 | 5 (installed 2018) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0473
United Utilities | PORT CARLISLE PUMPING STATION | Port Carlisle Pumping Station (Site ID PRTCA) (ALL0135) | 017680456 | ALL0135 | SO | Storm discharge at pumping station | NY2412162461 | 90 |  | THE SOLWAY FIRTH | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0.17 | 5 | 4.6667 | 6 (installed 2017) | 100 | [5 empty] | UUG0474
United Utilities | BOWNESS-ON-SOLWAY PUMPING STATION | Bowness on Solway PS | 017680457 | ALL0136 | SO | Storm discharge at pumping station | NY2251162891 | 90 |  | THE SOLWAY FIRTH | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 700.53 | 48 | 40.3333 | 6 (installed 2017) | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0475
United Utilities | WARRINGTON ROAD CSO | Warrington Road CSO | NPSWQD001822 | WIG0247 | SO | SO on sewer network | SJ6681098480 | 170 |  | BOWERS BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 9.2 | 5 (installed 2018) | 100 | [5 empty] | UUG0476
United Utilities | GRANGE OVER SANDS WWTW GRNGS | GRANGE-OVER-SANDS WwTW | 017370128 | 17370128 | SO | Inlet SO at WwTW | SD3926075060 | 184 |  | KENT CHANNEL MORECAMBE ESTUARY | 115 Morecambe Bay East | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 73.23 | 79 | 45 | 6 (installed 2017) | 99.93 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0477
United Utilities | MORECAMBE BANK CSO | Morecambe Bank CSO | 01LAK0071 | LAK0071 | SO | SO on sewer network | SD4087077860 | 184 |  | KENT CHANNEL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 12.47 | 20 | 41.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0478
United Utilities | RUNCORN ROAD CSO | RUNCORN ROAD CSO | 01HAL0057 | HAL0057 | SO | SO on sewer network | SJ5658083671 | GB112068060520 | Keckwick Brook | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 10.23 | 22 | 32.75 | 4 (installed 2019) | 100 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG0479
United Utilities | CART LANE PUMPING STATION | Cart Lane (Grange) PS | 017370129 | LAK0073 | SO | Storm discharge at pumping station | SD4027076810 | 184 |  | KENT CHANNEL | N/A | Morecambe North; Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 93.25 | 10 | 14.6667 | 6 (installed 2017) | 99.98 | [5 empty] | UUG0480
United Utilities | FIELD HEAD PUMPING STATION LAK0090 | Field Head Pumping Station (Site ID FLDHD) (LAK0090) | 017380283 | LAK0090 | SO | Storm discharge at pumping station | SD3660075500 | 181 |  | TRIB WINDERMOOR MAIN DRAIN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2083.7 | 178 | 163.8 | 5 (installed 2018) | 99.25 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0481
United Utilities | RAVENSTOWN PUMPING STATION | Ravenstown PS | 017380497 | LAK0103 | SO | Storm discharge at pumping station | SD3616074931 | 181 |  | WINDERMOOR MAIN DRAIN | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 24.5 | 7 | 12.3333 | 6 (installed 2017) | 99.88 | [5 empty] | UUG0482
United Utilities | DARESBURY COMBINED SEWER OVERFLOW | Daresbury CSO | 016921415 | HAL0089 | SO | SO on sewer network | SJ5784483338 | GB112068060520 | Keckwick Brook | DITCH TRIBUTARY RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.77 | 10 | 7.5 | 4 (installed 2019) | 100 | [5 empty] | UUG0483
United Utilities | SOUTH PARADE CSO 202S2 | South Parade CSO | 01HAL0106 | HAL0106 | SO | SO on sewer network | SJ4963081130 | GB531206908100 | MERSEY | WEAVER NAVIGATION | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.33 | 2 | 3 | 5 (installed 2018) | 100 | [5 empty] | UUG0484
United Utilities | SALTWORKS PUMPING STATION | ICI Saltworks PS | EPRQB3792NT | HAL0112 | SO | Storm discharge at pumping station | SJ4960081800 | GB531206908100 | MERSEY | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.25 | 2 | 2.75 | 4 (installed 2019) | 100 | [5 empty] | UUG0485
United Utilities | SHORE ROAD NETWORK PUMPING STATION | Shore Road Wastewater Network PS(Site ID 49065) (WLN0008) | 01WLN0008 | WLN0008 | SO | Storm discharge at pumping station | SD4375023810 | 175 |  | DUNKIRK DIB | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 106.4 | 57 | 26.8571 | 7 (installed 2016) | 99.8 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0486
United Utilities | HIGH LEGH STW | HIGH LEGH WwTW | 016910006 | 16910006 | SO | Inlet SO at WwTW | SJ7065083900 | 169 |  | AGDEN BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 71.99 | 17 | 20.3333 | 3 (installed 2020) | 99.9 | [5 empty] | UUG0487
United Utilities | KIRK BAMPTON WWTW (KIRKB) | KIRK BAMPTON WwTW | 017670126 | 17670126 | SO | Inlet SO at WwTW | NY3025057020 | 89 |  | BURGHMOOR BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1104.7 | 125 | 244 | 4 (installed 2019) | 99.46 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0488
United Utilities | FIR LANE COMBINED SEWER OVERFLOW | FIR LANE CSO | 01OLD0019 | OLD0019 | SO | SO on sewer network | SD9197009000 | GB112069061161 | Irk (Sourtce to Wince Brook) | UNNAMED TRIBUTARY OF RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 22.67 | 51 | 70.5 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0489
United Utilities | COWLISHAW CSO | Cowlishaw CSO | 016982851 | OLD0086 | SO | SO on sewer network | SD9313008350 | GB112069061161 | Irk (Sourtce to Wince Brook) | LUZLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 13.33 | 15 | 12.25 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0490
United Utilities | HOLDEN FOLD LANE CSO | Holden Fold Lane CSO | 016941057 | OLD0094 | SO | SO on sewer network | SD9161007190 | GB112069061161 | Irk (Sourtce to Wince Brook) | LUZLEY BRROK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 7.5 | 20 | 15.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0491
United Utilities | Royton Settled Storm Overflow | Royton Settled Storm Overflow | 16950043 | OLD0171 | ST | Storm tank at WwTW | SD9058907095 | GB112069061161 | Irk (Sourtce to Wince Brook) | RIVER IRK (VIA LUZLEY BK) | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 849.26 | 74 | 58.6667 | 3 (installed 2020) | 82.61 | Comms failure / issue | Scheduled | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0492
United Utilities | ROSTHWAITE WWTW (ROSTH) | ROSTHWAITE WwTW | 017570053 | 17570053 | SO | Inlet SO at WwTW | NY2548015050 | GB112075070330 | Derwent - headwaters to conf Stonethwaite Beck | TRIB OF RIVER DERWENT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 56.75 | 22 | 37.5 | 4 (installed 2019) | 99.89 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG0493
United Utilities | ROSSENDALE WWTW | ROSSENDALE WwTW | 016950042 | 16950042 | ST | Storm tank at WwTW | SD7957020610 | GB112069064641 | Irwell (Cowpe Bk to Rossendale STW) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1900.5 | 118 | 121.4 | 5 (installed 2018) | 61.71 | Comms failure / issue | Resolved - January after reporting year | Performance - Other maintenance / capital works (e.g. jetting) | Resolved - Jul | Other investigation - non-WINEP/Green Recovery | UUG0494
United Utilities | BANK ST COMBINED SEWER OVERFLOW | Bank Street CSO | 016993909 | ROS0001 | SO | SO on sewer network | SD8122022880 | GB112069064680 | Limy Water | LIMY WATER TRIB OF R IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 294.35 | 75 | 72.8 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0495
United Utilities | 709 BACUP ROAD CSO | OPPOSITE 709 BACUP ROAD CSO | 01ROS0007 | ROS0007 | SO | SO on sewer network | SD8335021830 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 10.5 | 7 | 4.75 | 4 (installed 2019) | 100 | [5 empty] | UUG0496
United Utilities | 295 BACUP ROAD CSO | 295 BACUP ROAD CSO | 01ROS0008 | ROS0008 | SO | SO on sewer network | SD8195022630 | GB112069064641 | Irwell (Cowpe Bk to Rossendale STW) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 407.5 | 68 | 66 | 4 (installed 2019) | 96.82 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Scheduled | Other investigation - non-WINEP/Green Recovery | UUG0497
United Utilities | NEW HALL HEY ROAD CSO | New Hall Hey Road CSO | 016993908 | ROS0009 | SO | SO on sewer network | SD8013022050 | GB112069064641 | Irwell (Cowpe Bk to Rossendale STW) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 34.76 | 19 | 12.5 | 4 (installed 2019) | 100 | [5 empty] | UUG0498
United Utilities | MANCHESTER RD DALESFORD RD 362EJ | Manchester Road/Dalesford Road | 01ROS0011 | ROS0011 | SO | SO on sewer network | SD7890022521 | GB112069064641 | Irwell (Cowpe Bk to Rossendale STW) | RVR IRWELL VIA LANGWOOD BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 100.73 | 81 | 86.25 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0499
United Utilities | NEWCHURCH ROAD/WESLEY PLACE CSO | NEWCHURCH ROAD / WESLEY PLACE CSO | 01ROS0013 | ROS0013 | SO | SO on sewer network | SD8650022060 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 113.63 | 59 | 44.75 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0500
United Utilities | ROCKLIFFE ROAD/RIVER STREET CSO | ROCKCLIFFE ROAD / RIVER STREET CSO | 01ROS0015 | ROS0015 | SO | SO on sewer network | SD8690022430 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.33 | 2 | 5 | 4 (installed 2019) | 100 | [5 empty] | UUG0501
United Utilities | 876 BURNLEY RD EAST CSO | 876 Burnley Road East CSO | 01ROS0006 | ROS0006 | SO | SO on sewer network | SD8366024720 | GB112069064670 | Whitewell Brook | WHITEWELL BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0502
United Utilities | WELLINGTON HOTEL CSO | WELLINGTON HOTEL CSO | 01ROS0017 | ROS0017 | SO | SO on sewer network | SD8700023100 | GB112069064660 | Irwell (Source to Whitewell Brook) | CULVERTED TRIB OF RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 1.8 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0503
United Utilities | WATERBARN LANE CSO | WATERBARN LANE CSO | 01ROS0018 | ROS0018 | SO | SO on sewer network | SD8450021710 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 37.77 | 15 | 8.75 | 4 (installed 2019) | 99.73 | [5 empty] | UUG0504
United Utilities | HAMMERTONSTREET/STANLEY STREET CSO | Hammerton Street/Stanley Street CSO | 01ROS0016 | ROS0016 | SO | SO on sewer network | SD8669023560 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Not Applicable | Dec 2023 | 34.6 | 71 |  | <1 yr (installed 2023) | 95.6757 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0505
United Utilities | SOUTH STREET/PICKUP STREET CSO | SOUTH STREET / PICKUP STREET CSO | 01ROS0020 | ROS0020 | SO | SO on sewer network | SD8694022940 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.63 | 6 | 6 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0506
United Utilities | BACUP ROAD/FALBARN FOLD CSO | Bacup Road/Markross Street CSO | 016993910 | ROS0024 | SO | SO on sewer network | SD8136022670 | GB112069064641 | Irwell (Cowpe Bk to Rossendale STW) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 964.19 | 118 | 97.75 | 4 (installed 2019) | 99.99 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Scheduled | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0507
United Utilities | HIGHFIELD ROAD CSO | Highfield Road CSO | 016993911 | ROS0025 | SO | SO on sewer network | SD8261022200 | GB112069064641 | Irwell (Cowpe Bk to Rossendale STW) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 82.85 | 24 | 16.75 | 4 (installed 2019) | 99.98 | [5 empty] | UUG0508
United Utilities | 143 BURNLEY ROAD EAST CSO | 143 Burnley Road East CSO | 016993566 | ROS0026 | SO | SO on sewer network | SD8371022300 | GB112069064670 | Whitewell Brook | WHITEWELL BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 179.27 | 40 | 49.25 | 4 (installed 2019) | 96.79 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0509
United Utilities | BURNLEY ROAD EAST/SHAWCLOUGH CSO | Burnley Road East/Shawclough Road CSO | 01ROS0027 | ROS0027 | SO | SO on sewer network | SD8362023210 | GB112069064670 | Whitewell Brook | WHITEWLL BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.83 | 1 | 1.5 | 4 (installed 2019) | 99.98 | [5 empty] | UUG0510
United Utilities | BURNLEY RD E /WHITEWELL BOTTOM CSO | Burnley Road East/Whitewall Bottom CSO | 016993743 | ROS0028 | SO | SO on sewer network | SD8349023870 | GB112069064670 | Whitewell Brook | WHITEWELL BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.93 | 2 | 2 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0511
United Utilities | BURNLEY ROAD EAST/TOWNLEY ARMS CSO | Burnley Road East/Townley Arms CSO | 016993545 | ROS0029 | SO | SO on sewer network | SD8392025240 | GB112069064670 | Whitewell Brook | WHITEWELL BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 11.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0512
United Utilities | THE GLEN COMBINED SEWER OVERFLOW | The Glen CSO | 016993608 | ROS0030 | SO | SO on sewer network | SD8409021650 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1842.21 | 179 | 152 | 4 (installed 2019) | 95.3 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Scheduled | Other investigation - non-WINEP/Green Recovery | UUG0513
United Utilities | BLACKWOOD ROAD CSO | Blackwood Road | 01ROS0031 | ROS0031 | SO | SO on sewer network | SD8527021620 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.17 | 2 | 2.5 | 4 (installed 2019) | 99.3 | [5 empty] | UUG0514
United Utilities | NEWCHURCH ROAD/BROOKS STREET CSO | NEWCHURCH ROAD / BROOKS STREET CSO | 01ROS0032 | ROS0032 | SO | SO on sewer network | SD8593021780 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 556.83 | 108 | 107.75 | 4 (installed 2019) | 98.44 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0515
United Utilities | NEWCHURCH ROAD BACUP CSO | NEWCHURCH ROAD (Bacup) CSO | 01ROS0033 | ROS0033 | SO | SO on sewer network | SD8625021820 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2.8 | 10 | 13.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0516
United Utilities | BURNLEY ROAD BACUP CSO | BURNLEY ROAD (BACUP) CSO | 01ROS0034 | ROS0034 | SO | SO on sewer network | SD8668023570 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2.13 | 2 | 8.75 | 4 (installed 2019) | 100 | [5 empty] | UUG0517
United Utilities | CARR MILL STREET CSO | Carr Mill Street/Hud Hey Road CSO | 016993764 | ROS0035 | SO | SO on sewer network | SD7858024380 | GB112069064650 | Ogden | CLVRT'D SECTION SWINNEL BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 329.11 | 74 | 69.5 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0518
United Utilities | HELMSHORE CARAVAN PARK CSO | Helmshore Caravan Park combined sewer overflow | 01ROS0036 | ROS0036 | SO | SO on sewer network | SD7784022060 | GB112069064650 | Ogden | SWINNEL BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 351.02 | 71 | 62.8 | 5 (installed 2018) | 98.92 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0519
United Utilities | LANGWOOD BROOK CSO | Langwood Brook CSO | 016993533 | ROS0037 | SO | SO on sewer network | SD7900022740 | GB112069064641 | Irwell (Cowpe Bk to Rossendale STW) | CLVRT'D SECTION LANGWOOD BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 10.6 | 13 | 19.5 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0520
United Utilities | MANCHESTER RD CSO (363F2) | Manchester Road (Bent Street) CSO | 01ROS0038 | ROS0038 | SO | SO on sewer network | SD7937022010 | GB112069064641 | Irwell (Cowpe Bk to Rossendale STW) | CULVERTED LANGWOOD BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0.66667 | 3 (installed 2020) | 100 | [5 empty] | UUG0521
United Utilities | TONG LANE/REED STREET CSO | TONG LANE / REED STREET CSO | 01ROS0019 | ROS0019 | SO | SO on sewer network | SD8710023170 | GB112069064660 | Irwell (Source to Whitewell Brook) | GLEAVE CLOUGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0.25 | 4 (installed 2019) | 98.23 | [5 empty] | UUG0522
United Utilities | BURNLEY RD E/BOOTH ST CSO | Burnley Road East/Booth Street CSO | 01ROS0041 | ROS0041 | SO | SO on sewer network | SD8339021940 | GB112069064670 | Whitewell Brook | WHITEWELL BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.33 | 2 | 9 | 4 (installed 2019) | 100 | [5 empty] | UUG0523
United Utilities | COWDE RD BR. | Cowpe Road SSO | 01ROS0042 | ROS0042 | SO | SO on sewer network | SD8344021730 | GB112069064660 | Irwell (Source to Whitewell Brook) | River Irwell | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 5.47 | 5 | 15.25 | 4 (installed 2019) | 99.98 | [5 empty] | UUG0524
United Utilities | DEARDENGATE/BURY ROAD CSO | DEARDENGATE / BURY ROAD CSO | 01ROS0039 | ROS0039 | SO | SO on sewer network | SD7808023251 | GB112069064650 | Ogden | SWINNEL BROOK | N/A | N/A | Not Applicable | Dec 2023 | 2979.87 | 168 |  | <1 yr (installed 2023) | 37.3874 | Installation set-up/design issue | N/A - Ongoing investigation | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0525
United Utilities | MANCHESTER ROAD SEWER | Manchester Road Sewer | 01ROS0058 | ROS0058 | SO | SO on sewer network | SD7808023252 | GB112069064650 | Ogden | Swinnel Brook | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0526
United Utilities | IRWELL VALE PS | Irwell Vale PS | 016982826 | ROS0073 | SO | Storm discharge at pumping station | SD7906020460 | GB112069064650 | Ogden | RIVER OGDEN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 369 | 64 | 30.3333 | 3 (installed 2020) | 72.93 | Comms failure / issue | Resolved - January after reporting year | Data collection - EDM non-representative location | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0527
United Utilities | RUSHBED SSO | Rushbed SSO | 016982214 | ROS0069 | SO | SO on sewer network | SD8097024840 | GB112069064680 | Limy Water | LIMY WATER | N/A | N/A | Not Applicable | Dec 2023 | 15.27 | 39 |  | <1 yr (installed 2023) | 96.14 | [5 empty] | UUG0528
United Utilities | NEW HALL HEY BRIDGE CSO | New Hall Hey Bridge CSO | 016982933 | ROS0075 | SO | SO on sewer network | SD8095022410 | GB112069064641 | Irwell (Cowpe Bk to Rossendale STW) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 16.93 | 14 | 37 | 3 (installed 2020) | 99.99 | [5 empty] | UUG0529
United Utilities | GREAVE CLOUGH DRIVE CSO | Greave Clough Drive CSO | 016982934 | ROS0076 | SO | SO on sewer network | SD8749023220 | GB112069064660 | Irwell (Source to Whitewell Brook) | GREAVE CLOUGH VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0530
United Utilities | LEE ROAD CSO (369BA) | Lee Road CSO | 016982935 | ROS0077 | SO | SO on sewer network | SD8625021810 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.23 | 2 | 1 | 3 (installed 2020) | 99.54 | [5 empty] | UUG0531
United Utilities | NEWCHURCH ROAD CSO (36013) | Newchurch Road CSO | NPSWQD006555 | ROS0082 | SO | SO on sewer network | SD8461021740 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 457.5 | 51 | 44.3333 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0532
United Utilities | BURNLEY RD/MIDDLEGATE CSO | Burnley Road/Middlegate CSO | 016982931 | ROS0078 | SO | SO on sewer network | SD8095026100 | GB112069064680 | Limy Water | LIMY WATER TRIB OF IRWELL | N/A | N/A | Not Applicable | Dec 2023 | 101.07 | 26 |  | <1 yr (installed 2023) | 97.39 | [5 empty] | UUG0533
United Utilities | BRYN ROAD | Bryn Road CSO | 01WIG0104 | WIG0104 | SO | SO on sewer network | SJ5857098960 | GB112069061220 | Millingford (Newton) Brook | MILLINGFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 37.29 | 59 | 57.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0534
United Utilities | ROCKLIFFE WWTW ROCKC | ROCKCLIFFE WwTW | 017670129 | 17670129 | ST | Storm tank at WwTW | NY3586061080 | GB530207614700 | SOLWAY | RIVER EDEN ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 959.52 | 99 | 76.6667 | 6 (installed 2017) | 100 |  |  | Data collection - Tidal / river inundation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0535
United Utilities | KIRK BAMPTON WWTW (KIRKB) | KIRK BAMPTON WwTW | 017670126 | 17670126 | ST | Storm tank at WwTW | NY3025057020 | 89 |  | BURGHMOOR BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2053.14 | 92 | 100.5 | 4 (installed 2019) | 99.9 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0536
United Utilities | ROCHDALE WWTW | ROCHDALE WWTW | 16950041 | 16950041 | ST | Storm tank at WwTW | SD8817012380 | GB112069064600 | Roch (Spodden to Irwell) | River Roch | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2491.86 | 155 | 91.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0537
United Utilities | SHAW MAIN OUTFALL | Newhey Shaw Main Outfall CSO | 01OLD0150 | OLD0150 | SO | SO on sewer network | SD9313011230 | GB112069064690 | Beal | RIVER BEAL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 568.76 | 54 | 40 | 4 (installed 2019) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity |  | UUG0538
United Utilities | Milnrow Road/Fishwick Street CSO | Milnrow Road/Fishwick Street CSO | EPR/QB3590VT/A001/2 | ROC0027 | SO | SO on sewer network | SD9048013128 | GB112069064720 | Roch (Source to Spodden) | Culverted section of Moss Brook a tributary of River Roch | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.97 | 7 | 5.75 | 4 (installed 2019) | 100 | [5 empty] | UUG0539
United Utilities | MELLOR STREET CSO | MELLOR STREET CSO | 01ROC0029 | ROC0029 | SO | SO on sewer network | SD8860013800 | GB112069064730 | Spodden | RIVER SPODDEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 1 | 4 (installed 2019) | 100 | [5 empty] | UUG0540
United Utilities | SMITH ST AND JOHN ST CSO 35021 | Junction of Smith Street/John Street CSO | 016993536 | ROC0039 | SO | SO on sewer network | SD9011013440 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 35.32 | 53 | 52.2 | 5 (installed 2018) | 71.03 | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0541
United Utilities | OAKCLIFFE ROAD CSO | Oakcliffe Road CSO | 016993527 | ROC0040 | SO | SO on sewer network | SD9159014540 | GB112069064690 | Beal | CULVERTED TRIB OF RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 39.03 | 47 | 46.5 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0542
United Utilities | STANNEY ROAD CSO | Stanney Road CSO | NPSWQD010735 | ROC0051 | SO | SO on sewer network | SD9127013620 | GB112069064720 | Roch (Source to Spodden) | STANNEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2.13 | 6 | 7.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0543
United Utilities | ST MARYS GATE/CHEETHAM STREET CSO | St. Mary's Gate / Cheetham Street CSO | EPRQB3591EA | ROC0055 | SO | SO on sewer network | SD8974013730 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | JOHNSON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 4.87 | 18 | 20.75 | 4 (installed 2019) | 95.13 | [5 empty] | UUG0544
United Utilities | NEWBOLD STREET CSO | Newbold Street CSO | NPSWQD008814 | ROC0057 | SO | SO on sewer network | SD9148013350 | GB112069064720 | Roch (Source to Spodden) | THE STANNEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 31.25 | 53 | 48.75 | 4 (installed 2019) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0545
United Utilities | YORKSHIRE STREET CSO 35022 | Yorkshire Street CSO | 01ROC0058 | ROC0058 | SO | SO on sewer network | SD8962013380 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.5 | 1 | 17 | 5 (installed 2018) | 96.56 | [5 empty] | UUG0546
United Utilities | ALBERT ROYDS STREET CSO | Albert Royds Street CSO | EPRSB3396NF | ROC0062 | SO | SO on sewer network | SD9098014360 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 76.4 | 35 | 48.6667 | 3 (installed 2020) | 45.22 | Comms failure / issue | Resolved - January after reporting year | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0547
United Utilities | ALBERT ROYDS STREET CSO | Albert Royds Street CSO | EPRQB3591WC | ROC0064 | SO | SO on sewer network | SD9100014400 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 53.53 | 19 | 16.75 | 4 (installed 2019) | 99.98 | [5 empty] | UUG0548
United Utilities | HARTLEY LANE CSO | Hartley Lane | EPRSB3396RE | ROC0066 | SO | SO on sewer network | SD8956011440 | GB112069064600 | Roch (Spodden to Irwell) | TRIB OF SUDDON BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 46.5 | 31 | 46 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0549
United Utilities | YORKSHIRE ST OSWALD ST CSO 35024 | Yorkshire Street / Oswald Street CSO | 016993538 | ROC0067 | SO | SO on sewer network | SD9044014030 | GB112069064720 | Roch (Source to Spodden) | HEY BROOK TRIB OF RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 48.78 | 50 | 49.2 | 5 (installed 2018) | 70.29 | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0550
United Utilities | BELFIELD ROAD/BESWICKE ROYDS ST CSO | Bellfield Road/Beswicke Royds Street | EPRQB3592VZ | ROC0069 | SO | SO on sewer network | SD9086014030 | GB112069064720 | Roch (Source to Spodden) | SANNEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 14.07 | 40 | 59.25 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0551
United Utilities | EDENFIELD ROAD CSO | Edenfield Road CSO | EPRQB3593DY | ROC0070 | SO | SO on sewer network | SD8579014610 | GB112069064710 | Naden Brook | NADEN BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.67 | 3 | 5.75 | 4 (installed 2019) | 99.98 | [5 empty] | UUG0552
United Utilities | BOND ST CSO | Bond Street CSO | EPRQB3592AV | ROC0065 | SO | SO on sewer network | SD9049014580 | GB112069064720 | Roch (Source to Spodden) | HEY BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0.75 | 4 (installed 2019) | 100 | [5 empty] | UUG0553
United Utilities | MILLGATE CSO 35025 | Millgate CSO | 01ROC0072 | ROC0072 | SO | SO on sewer network | SD9116014680 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 243.9 | 92 | 75.8 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0554
United Utilities | TRAFALGAR STREET /RAMSEY STREET CSO | Trafalgar Street/Ramsey Street Combined Sewer Overflow | NPSWQD010102 | ROC0071 | SO | SO on sewer network | SD9045013510 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 3.23 | 11 | 6.5 | 4 (installed 2019) | 96.25 | [5 empty] | UUG0555
United Utilities | DRAKE STREET CSO (35038) | Drake Street CSO | 01ROC0078 | ROC0078 | SO | SO on sewer network | SD8976013400 | GB112069064720 | Roch (Source to Spodden) | CULVERTED RIVER ROCH VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 13.22 | 35 | 28.6667 | 3 (installed 2020) | 97.34 | [5 empty] | UUG0556
United Utilities | OAKENROD COMBINED SEWER OVERFLOW | OAKENROD CSO | 016982276 | ROC0080 | SO | SO on sewer network | SD8879013050 | GB112069064600 | Roch (Spodden to Irwell) | RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1130.84 | 129 | 110.75 | 4 (installed 2019) | 96.66 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0557
United Utilities | ROOLEY MOOR RD W51 | Rooley Moor Road | 01ROC0077 | ROC0077 | SO | SO on sewer network | SD8792014450 | GB112069064730 | Spodden | TRIB HEALEY DELL | N/A | N/A | Not Applicable | Dec 2023 | 131.53 | 49 |  | <1 yr (installed 2023) | 97.58 | [5 empty] | UUG0558
United Utilities | MANCHESTER RD CSO (351TT) | Manchester Road (Near the Esplanade) CSO | 01ROC0082 | ROC0082 | SO | SO on sewer network | SD8934013200 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 4.33 | 20 | 6.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0559
United Utilities | OLDHAM ROAD CSO 35027 | Oldham Road CSO | 01ROC0093 | ROC0093 | SO | SO on sewer network | SD9060010840 | GB112069064600 | Roch (Spodden to Irwell) | CLVRT SEC OF SUDDEN BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 371 | 96 | 101 | 5 (installed 2018) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0560
United Utilities | WATER STREET CSO | Water Street | EPRQB3593RF | ROC0097 | SO | SO on sewer network | SD9006013400 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 4.53 | 22 | 24.75 | 4 (installed 2019) | 100 | [5 empty] | UUG0561
United Utilities | SPOTLAND BRIDGE CSO 35035 | Spotland Bridge CSO | 016981350 | ROC0099 | SO | SO on sewer network | SD8861013830 | GB112069064730 | Spodden | RIVER SPODDEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 237.21 | 89 | 82.6 | 5 (installed 2018) | 91.33 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0562
United Utilities | MILNROW ROAD/FISHWICK STREET CSO | Milnrow Road CSO | 016993541 | ROC0103 | SO | SO on sewer network | SD9050012920 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 93.58 | 90 | 91.75 | 4 (installed 2019) | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0563
United Utilities | SMITH BRIDGE ROAD CSO 35051 | Smithy Bridge Road CSO | 01ROC0122 | ROC0122 | SO | SO on sewer network | SD9241015390 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 330.6 | 38 | 29.2 | 5 (installed 2018) | 99.93 | [5 empty] | UUG0564
United Utilities | MILNROW ROAD/PINE STREET CSO | Milnrow Road/Pine Street | EPRSB3396VR | ROC0091 | SO | SO on sewer network | SD9050013260 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1.23 | 6 | 2 | 3 (installed 2020) | 88.64 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0565
United Utilities | GREENBANK ROAD/ROSSALL ROAD CSO | Greenbank Road | EPRQB3593VE | ROC0127 | SO | SO on sewer network | SD8998014560 | GB112068060460 | Roch (Source to Spodden) | Culverted Section of Foxholes Brook | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0 | 0 | 0.66667 | 6 (installed 2017) | 99.96 | [5 empty] | UUG0566
United Utilities | TOAD LANE - HIGH STREET CSO | Toad Lane - High Street CSO | 016950161 | ROC0140 | SO | SO on sewer network | SD8928013340 | GB112069064720 | Roch (Source to Spodden) | RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 3.83 | 14 | 13 | 4 (installed 2019) | 100 | [5 empty] | UUG0567
United Utilities | WATERHOUSE CLOSE (WARDLE) CSO | Waterhouse Close (Wardle) CSO | 016950075 | ROC0138 | SO | SO on sewer network | SD9138016430 | GB112069064720 | Roch (Source to Spodden) | ASH BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 28.27 | 34 | 22.75 | 4 (installed 2019) | 91.51 | [5 empty] | UUG0568
United Utilities | SUDDEN VALLEY SEWER | Sudden Valley SSO | 016981577 | ROC0156 | SO | SO on sewer network | SD8819012280 | GB112069064600 | Roch (Spodden to Irwell) | RIVER ROCH | N/A | N/A | Not Applicable | Dec 2023 | 92.39 | 23 |  | <1 yr (installed 2023) | 99.99 | [5 empty] | UUG0569
United Utilities | MARLAND HILL SSO | Marland Hill SSO | 01ROC0157 | ROC0157 | SO | SO on sewer network | SD8819012282 | GB112069064600 | Roch (Spodden to Irwell) | River Roch | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0570
United Utilities | ASHES LANE CSO | Field West of Ashes Lane CSO | 016982641 | ROC0163 | SO | SO on sewer network | SD9237013250 | GB112069064690 | Beal | RIVER BEAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1230.97 | 81 | 66.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0571
United Utilities | FOOTWOOD / SPODDEN VALLEY CSO | Shawclough Brook CSO | 016982516 | ROC0169 | SO | SO on sewer network | SD8870014380 | GB112069064730 | Spodden | RIVER SPODDEN, TRIB RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 498.43 | 61 | 56.25 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0572
United Utilities | DYEHOUSE LANE CSO | Dyehouse Lane CSO | 016982937 | ROC0170 | SO | SO on sewer network | SD9131015060 | GB112069064720 | Roch (Source to Spodden) | ASH BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 33.13 | 20 | 21 | 4 (installed 2019) | 99.15 | [5 empty] | UUG0573
United Utilities | SHAW ROAD CSO | Shaw Road CSO | 016982938 | ROC0172 | SO | SO on sewer network | SD9326011200 | GB112069064690 | Beal | RIVER BEAL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.23 | 1 | 7.75 | 4 (installed 2019) | 94.68 | [5 empty] | UUG0574
United Utilities | NORDEN/BAMFORD OUTFALL SEWER | Norden/Bamford Outfall SSO | 01ROC0159 | ROC0159 | SO | SO on sewer network | SD8762012590 | GB112069064600 | Roch (Spodden to Irwell) | River Roch | N/A | N/A | Not Applicable | Dec 2023 | 410.19 | 89 |  | <1 yr (installed 2023) | 88.52 | Installation set-up/design issue | N/A - Ongoing investigation | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0575
United Utilities | 745 EDENFIELD ROAD CSO | 745 Edenfield Road CSO | 016997072 | ROC0188 | SO | SO on sewer network | SD8583014620 | GB112069064710 | Naden Brook | NADEN BROOK TRIB OF R ROCH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 2.75 | 4 (installed 2019) | 99.98 | [5 empty] | UUG0576
United Utilities | PEPPERMINT BRIDGE CSO | Peppermint Bridge CSO | EPRJB3896EL | ROC0192 | SO | SO on sewer network | SD9437211958 | GB112069064690 | Beal | PIETHORNE BROOK TRIB RVR BEAL | N/A | N/A | Not Applicable | Dec 2023 | 0.2 | 1 |  | <1 yr (installed 2023) | 66.6667 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0577
United Utilities | STATION ROAD (WHITWORTH) CSO | Station Road (Whitworth) CSO | 01ROS0044 | ROS0044 | SO | SO on sewer network | SD8804016380 | GB112069064730 | Spodden | RIVER SPODDEN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 2.8 | 6 | 4.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0578
United Utilities | WHITWORTH CSO | 100Metres East of No. XX Eastgate CSO | 016950442 | ROS0062 | SO | SO on sewer network | SD8814017070 | GB112069064730 | Spodden | RIVER SPODDEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 556.63 | 84 | 74 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0579
United Utilities | WHITWORTH SSO | Cowm Park Way South | 016950443 | ROS0063 | SO | SO on sewer network | SD8830017880 | GB112069064730 | Spodden | RIVER SPODDEN | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0580
United Utilities | OUGHTERBY PUMPING STATION | Oughterby Pumping Station (Site ID 02587) (ALL0067) | 01ALL0067 | ALL0067 | SO | Storm discharge at pumping station | NY2921055660 | 89 |  | UNNAMED TRIB. OF GRASS DYKE | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 44.05 | 7 | 5.8333 | 6 (installed 2017) | 99.99 | [5 empty] | UUG0581
United Utilities | RIBCHESTER WWTW | RIBCHESTER WwTW | 017160043 | 17160043 | SO | Inlet SO at WwTW | SD6516034401 | GB112071065500 | Ribble - conf Calder to tidal | RIVER RIBBLE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 86.31 | 6 | 10.6 | 5 (installed 2018) | 98.53 | [5 empty] | UUG0582
United Utilities | RIBCHESTER WWTW | RIBCHESTER WwTW | 017160043 | 17160043 | ST | Storm tank at WwTW | SD6516034401 | GB112071065500 | Ribble - conf Calder to tidal | RIVER RIBBLE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 156.8 | 14 | 74.2 | 5 (installed 2018) | 83.01 | Comms failure / issue | Resolved - January after reporting year | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0583
United Utilities | RENWICK CSO (171MD) | Renwick CSO | 017680333 | EDE0084 | SO | SO on sewer network | NY5954043250 | GB102076073840 | Raven Beck | HARBERRY BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 6.7 | 20 | 12.6667 | 3 (installed 2020) | 99.89 | [5 empty] | UUG0584
United Utilities | RAVENSTONEDALE STW | RAVENSTONEDALE WwTW | 017670024 | 17670024 | SO | Inlet SO at WwTW | NY7212004600 | GB102076070600 | Scandal Beck | SANDAL BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1629.4 | 126 | 142.3333 | 3 (installed 2020) | 99.73 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0585
United Utilities | EJEC STN, NEWBIGGIN-ON-LUNE | Newbiggin-on-Lune Wastewater Network Pumping Station | 01EDE0065 | EDE0065 | SO | Storm discharge at pumping station | NY7034005380 | GB112072071760 | Lune - headwaters to conf Birk Beck | Lune - headwaters to conf Birk Beck | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 226.85 | 45 | 32 | 3 (installed 2020) | 99.95 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0586
United Utilities | KIRKBRIDE WWTW | Kirkbride Wastewater Treatment Works (Site ID KRKBR) (017570195) | 017580195 | 17570195 | ST | Storm tank at WwTW | NY2365056890 | 90 |  | RIVER WAMPOOL | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 1234.51 | 110 | 60.2857 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0587
United Utilities | PROSPECT AND OUGHTERSIDE WWTW PRSPO | PROSPECT & OUGHTERSIDE WwTW | 017570073 | 17570073 | SO | Inlet SO at WwTW | NY1170040020 | GB112075073640 | Ellen (lower) | SALTERWATH BECK | N/A | Allonby | Not Applicable | Commissioned in 2017 - full year data expected | 672.1 | 131 | 127.5 | 6 (installed 2017) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0588
United Utilities | LUNE STREET PUMPING STATION 25030 | Lune Street Sewage PS | 017270195 | LAN0007 | SO | Storm discharge at pumping station | SD4757062170 | 178 |  | RIVER LUNE ESTUARINE WATERS | N/A | Morecambe North | Not Applicable | Commissioned in 2016 - full year data expected | 595.41 | 30 | 40.5714 | 7 (installed 2016) | 65.94 | Telemetry or data archiving failure / issue | Resolved - Nov | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Resolved - Jul | Other investigation - non-WINEP/Green Recovery | UUG0589
United Utilities | BULK ROAD CSO 25097 | Bulk Road CSO (25097) | 017280370 | LAN0018 | SO | SO on sewer network | SD4799062091 | 178 |  | RIVER LUNE EST (VIA MILL RACE) | N/A | Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 18.25 | 10 | 20.1667 | 6 (installed 2017) | 100 | [5 empty] | UUG0590
United Utilities | CABLE STREET CSO 251H9 | Cable Street Combined Sewer Overflow (Site ID 251H9) (LAN0020) | 017280369 | LAN0020 | SO | SO on sewer network | SD4761061941 | 178 |  | LUNE ESTUARY | N/A | Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 493.98 | 47 | 24.6667 | 6 (installed 2017) | 83.64 | Installation set-up/design issue | N/A - Ongoing investigation | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0591
United Utilities | BALLAM ROAD PUMPING STATION | Ballam Road PS | 017180610 | FYL0004 | SO | Storm discharge at pumping station | SD3668027570 | GB112071065650 | Liggard Brook | LIGGARD BROOK | N/A | St Annes Pier; St. Annes North; Blackpool South | Not Applicable | Commissioned in 2017 - full year data expected | 31.84 | 22 | 26.8333 | 6 (installed 2017) | 100 | [5 empty] | UUG0592
United Utilities | SCALE HALL PUMPING STATION | Scale Hall PS | 017270196 | LAN0039 | SO | Storm discharge at pumping station | SD4643062240 | 178 |  | LUNE ESTUARY | N/A | Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 400.61 | 41 | 78.6667 | 6 (installed 2017) | 38.7 | Comms failure / issue | Resolved - January after reporting year | Data collection - EDM non-representative location | Resolved - Nov | Other investigation - non-WINEP/Green Recovery | UUG0593
United Utilities | SCHOOL LANE CSO 192QK | School Lane CSO | 017160084 | FYL0006 | SO | SO on sewer network | SD4300032460 | GB112070064912 | Lostock DS Farington Weir | CARR BROOK | N/A | St Annes | Not Applicable | Commissioned in 2018 - full year data expected | 0.47 | 4 | 25 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0594
United Utilities | STATION ROAD CSO 19084 | Station Road CSO | 017190852 | FYL0014 | SO | SO on sewer network | SD4180032600 | GB112071065670 | Dow Brook | WRONGWAY BROOK | N/A | St Annes | Not Applicable | Commissioned in 2018 - full year data expected | 325.27 | 31 | 32.2 | 5 (installed 2018) | 99.85 | [5 empty] | UUG0595
United Utilities | ROSEMARY LANE CSO 252PG | Rosemary Lane CSO | 017280276 | LAN0075 | SO | SO on sewer network | SD4782061820 | 178 |  | MILL RACE | N/A | Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 337.87 | 33 | 23.6667 | 6 (installed 2017) | 100 | [5 empty] | UUG0596
United Utilities | NEAR SHIP INN CSO | Near the Ship Inn CSO | 017190859 | FYL0016 | SO | SO on sewer network | SD4360028701 | GB112071065670 | Dow Brook | DOW BROOK TRIB OF FRECKLTON PL | N/A | St Annes | Not Applicable | Commissioned in 2018 - full year data expected | 149.2 | 61 | 47.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0597
United Utilities | DOW BRIDGE CSO 19080 | Dow Bridge CSO (19080) | 017190860 | FYL0017 | SO | SO on sewer network | SD4360031700 | GB112071065670 | Dow Brook | DOW BROOK | N/A | St Annes | Not Applicable | Commissioned in 2018 - full year data expected | 72.57 | 10 | 10.2 | 5 (installed 2018) | 100 | [5 empty] | UUG0598
United Utilities | DAMSIDE SCREENING CSO 25076 | Damside Screening Chamber CSO | 017280278 | LAN0078 | SO | SO on sewer network | SD4754062030 | 178 |  | MILL RACE | N/A | Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 55.59 | 28 | 24.3333 | 6 (installed 2017) | 100 | [5 empty] | UUG0599
United Utilities | LYTHAM ROAD | Warton Pumping Station (Site id 19010) (FYL0028) | NPSWQD010748 | FYL0028 | SO | Storm discharge at pumping station | SD3820028200 | GB112071065651 | Main Drain (Ribble) | WREA BROOK | N/A | Southport; St Annes Pier; St. Annes North; Blackpool South | Not Applicable | Commissioned in 2017 - full year data expected | 278.06 | 69 | 55.3333 | 6 (installed 2017) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0600
United Utilities | SMITHY LANE PUMPING STATION 19003 | Smithy Lane PS | 01FYL0011 | FYL0011 | SO | Storm discharge at pumping station | SD3420029400 | GB112071065650 | Liggard Brook | UNNAMED TRIB LAGGARD BROOK | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 0 | 0 | 0 | 7 (installed 2016) | 100 | [5 empty] | UUG0601
United Utilities | WILLOW LANE SEWAGE PUMPING STATION | Willow Lane Sewage P/S (25032) | 017280342 | LAN0106 | SO | Storm discharge at pumping station | SD4665962201 | 178 |  | RIVER LUNE ESTUARY | N/A | Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 134.75 | 30 | 30.6667 | 6 (installed 2017) | 99.82 | [5 empty] | UUG0602
United Utilities | MEATHOP PUMPING STATION | Meathop PS | 017380417 | LAK0102 | SO | Storm discharge at pumping station | SD4415080530 | 183 |  | MEATHOP MARSH DRAIN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 360.19 | 26 | 17 | 4 (installed 2019) | 95.02 | [5 empty] | UUG0603
United Utilities | KIRKHAM COMBINED SEWER OVERFLOW | Kirkham CSO | 017180578 | FYL0044 | SO | SO on sewer network | SD4248032450 | GB112071065670 | Dow Brook | CARR BROOK, TRIB. OF DOW BROOK | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 73.33 | 18 | 23.4286 | 7 (installed 2016) | 100 | [5 empty] | UUG0604
United Utilities | MOWBRECK WW NTWK PS | Mowbreck Ww Ntwk PS | 01FYL0036 | FYL0036 | SO | Storm discharge at pumping station | SD4270033200 | GB112071065670 | Dow Brook | UNNAMED TRIB OF CARR BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0605
United Utilities | LIVERPOOL WWTW | LIVERPOOL WwTW | 016993397 | 16993397 | SO | Inlet SO at WwTW | SJ3321092640 | 167 |  | RIVER MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 998.84 | 110 | 110.7143 | 7 (installed 2016) | 60 | Sensor failure / issue | Resolved - January after reporting year | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0606
United Utilities | LIVERPOOL WWTW | LIVERPOOL WwTW | 016993397 | 16993397 | ST | Storm tank at WwTW | SJ3321092640 | 167 |  | RIVER MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 1356.11 | 90 | 33 | 7 (installed 2016) | 99.75 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0607
United Utilities | HALE VILLAGE PUMPING STATION | Hale Village PS | 016920551 | HAL0093 | SO | Storm discharge at pumping station | SJ4747082910 | 167 |  | RAM'S BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 151.75 | 62 | 60.25 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0608
United Utilities | HALE ROAD / DINNER LANE CSO | Hale Road/Dinner Lane | 016982704 | HAL0123 | SO | SO on sewer network | SJ4633082310 | 167 |  | LADY POOL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 59 | 15 | 13.5 | 4 (installed 2019) | 99.73 | [5 empty] | UUG0609
United Utilities | SHAROE GREEN HOSPITAL CSO 333JK | Sharoe Green Hospital CSO | 01PRE0012 | PRE0012 | SO | SO on sewer network | SD5376031960 | GB112071065470 | Savick Brook | SAVICK BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 110.4 | 84 | 72.4 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0610
United Utilities | COW HILL CLARKSONS FOLD CSO 33100 | Cow Hill Lane, Preston CSO (33100) | 017190863 | PRE0015 | SO | SO on sewer network | SD5705034030 | GB112071065470 | Savick Brook | SAVICK BROOK TRIB RVR RIBBLE | N/A | St Annes | Not Applicable | Commissioned in 2018 - full year data expected | 113.7 | 11 | 7.6 | 5 (installed 2018) | 100 | [5 empty] | UUG0611
United Utilities | 75 LOWER BANK ROAD CSO | 75 LOWER BANK ROAD CSO | 01PRE0017 | PRE0017 | SO | SO on sewer network | SD5409031320 | GB112071065470 | Savick Brook | EAVES BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 1 | 4 (installed 2019) | 91.84 | [5 empty] | UUG0612
United Utilities | ST NICHOLAS STORM SEWER OVERFLOW | St. Nicholas Storm Sewer overflow | 016930973 | LIV0027 | SO | SO on sewer network | SJ3370090400 | 185 |  | MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2017 - full year data expected | 1.27 | 13 | 13.5 | 6 (installed 2017) | 100 | [5 empty] | UUG0613
United Utilities | PARK STREET COMBINED SEWER OVERFLOW | Park Street SO | 016930977 | LIV0028 | SO | SO on sewer network | SJ3470088000 | 167 |  | RIVER MERSEY ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.01 | 1 | 5.5 | 4 (installed 2019) | 100 | [5 empty] | UUG0614
United Utilities | BANKHALL RELIEF CSO 99006 | Northern CSO | 016930968 | LIV0037A | SO | SO on sewer network | SJ3300093900 | 167 |  | RIVER MERSEY ESTUARINE WATERS | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 47.79 | 41 | 37.4286 | 7 (installed 2016) | 99.98 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0615
United Utilities | BANKHALL RELIEF CSO 99005 | Bankhall Relief CSO | 016930968 | LIV0037B | SO | SO on sewer network | SJ3300093900 | 167 |  | RIVER MERSEY ESTUARINE WATERS | N/A | Wallasey | Not Applicable | Commissioned in 2016 - full year data expected | 7.34 | 30 | 19 | 7 (installed 2016) | 99.98 | [5 empty] | UUG0616
United Utilities | SANDHILLS LANE CSO | Sandhills Lane CSO | 016930970 | LIV0039 | SO | SO on sewer network | SJ3320093101 | 167 |  | MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 2.29 | 6 | 15.8571 | 7 (installed 2016) | 99.69 | [5 empty] | UUG0617
United Utilities | BEACONS GUTTER SSO | Beacons Gutter CSO | 016930971 | LIV0040 | SO | SO on sewer network | SJ3320092700 | 167 |  | RIVER MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 1.47 | 12 | 10.2857 | 7 (installed 2016) | 99.72 | [5 empty] | UUG0618
United Utilities | BATTERY LANE CSO | Battery Lane CSO | 016930972 | LIV0041 | SO | SO on sewer network | SJ3320092000 | 167 |  | MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 0.7 | 6 | 4.5714 | 7 (installed 2016) | 100 | [5 empty] | UUG0619
United Utilities | DINGLE COMBINED SEWER OVERFLOW | Dingle CSO | 016930978 | LIV0042 | SO | SO on sewer network | SJ3570086900 | 167 |  | MERSEY ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 82.79 | 62 | 50.75 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0620
United Utilities | FULWOOD CSO | Fulwood CSO | 016930980 | LIV0043 | SO | SO on sewer network | SJ3720086000 | 167 |  | RIVER MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 0.52 | 2 | 3.7143 | 7 (installed 2016) | 100 | [5 empty] | UUG0621
United Utilities | 2 MILL LANE COMBINED SEWER OVERFLOW | 2 Mill Lane CSO | 01PRE0031 | PRE0031 | SO | SO on sewer network | SD5250031380 | GB112071065470 | Savick Brook | SAVICK BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 31.4 | 9 | 12 | 4 (installed 2019) | 100 | [5 empty] | UUG0622
United Utilities | GARSTANG ROAD BRIDGE CSO 333EH | Garstang Road Bridge CSO | 01PRE0034 | PRE0034 | SO | SO on sewer network | SD5327031770 | GB112071065470 | Savick Brook | SAVICK BROOK | N/A | St Annes | Not Applicable | Commissioned in 2018 - full year data expected | 23.6 | 13 | 11.2 | 5 (installed 2018) | 94.62 | [5 empty] | UUG0623
United Utilities | WATERY LANE FORMER PS CSO 339DQ | Watery Lane PS CSO | 016982541 | PRE0036 | SO | SO on sewer network | SD5215429748 | GB112069061170 | Sutton Brook | SUTTON BROOK | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 0 | 0 | 2 | 7 (installed 2016) | 100 | [5 empty] | UUG0624
United Utilities | BLACK BULL MH C1 CSO 331EQ | Black Bull Lane M/H C1 | EPRKB3991VZ | PRE0053 | SO | SO on sewer network | SD5285631518 | GB112071065470 | Savick Brook | SAVICK BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 10.3 | 4 | 3 | 5 (installed 2018) | 100 | [5 empty] | UUG0625
United Utilities | WINDBOURNE CSO | Windbourne CSO | 01LIV0044 | LIV0044 | SO | SO on sewer network | SJ3678086240 | 167 |  | RIVER MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 10.68 | 10 | 10.2857 | 7 (installed 2016) | 100 | [5 empty] | UUG0626
United Utilities | GRIMSARGH CSO 333LG | Grimsargh CSO | 01PRE0061 | PRE0061 | SO | SO on sewer network | SD5896034240 | GB112071065500 | Ribble - conf Calder to tidal | TRIB TUN BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.1 | 1 | 28.2 | 5 (installed 2018) | 100 | [5 empty] | UUG0627
United Utilities | CATTLE MARKET CSO | Cattle Market CSO | 017180626 | PRE0065 | SO | SO on sewer network | SD5279031260 | GB112071065470 | Savick Brook | EAVES BK, TRIB OF SAVICK BK | N/A | N/A | Not Applicable | Dec 2023 | 661.1 | 37 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0628
United Utilities | MANOR HOUSE LANE CSO 33037 | Manor House Lane CSO | 017180627 | PRE0069 | SO | SO on sewer network | SD5531031490 | GB112071065470 | Savick Brook | EAVES BK, TRIB OF SAVICK BK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 515.72 | 42 | 8.4 | 5 (installed 2018) | 99.98 |  |  | Data collection - EDM non-representative location | N/A - Ongoing investigation |  | UUG0629
United Utilities | BANKHALL CSO 99007 LIV0038 | Bankhall CSO | 016930969 | LIV0038 | SO | SO on sewer network | SJ3320093500 | 167 |  | RIVER MERSEY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 1.33 | 10 | 6.8571 | 7 (installed 2016) | 99.73 | [5 empty] | UUG0630
United Utilities | SOUTHERN RELIEF CSO | Southern Relief CSO | 016930984 | LIV0051 | SO | SO on sewer network | SJ3835085050 | 167 |  | MERSEY ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 206.11 | 66 | 66.5 | 4 (installed 2019) | 99.73 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0631
United Utilities | MERSEY ROAD COMBINED SEWER OVERFLOW | Mersey Road CSO | 016930983 | LIV0052 | SO | SO on sewer network | SJ3808085270 | 167 |  | MERSEY ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 46.86 | 40 | 34.5 | 4 (installed 2019) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0632
United Utilities | GRASSENDALE COMBINED SEWER OVERFLOW | Grassendale CSO | 016930985 | LIV0053 | SO | SO on sewer network | SJ3853084780 | 167 |  | MERSEY ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 13.77 | 11 | 20.75 | 4 (installed 2019) | 99.73 | [5 empty] | UUG0633
United Utilities | LOWER TABLEY PUMPING STATION | Lower Tabley PS | 01PRE0079 | PRE0079 | SO | SO on sewer network | SD4987034190 | GB112072065760 | Woodplumpton Brook | WOODPLUMPTON BROOK | N/A | N/A | Not Applicable | Dec 2023 | 331.78 | 53 |  | <1 yr (installed 2023) | 94.2308 | [5 empty] | UUG0634
United Utilities | JERICHO LANE CSO | Jericho Lane CSO | 016930981 | LIV0045 | SO | SO on sewer network | SJ3740085810 | 167 |  | MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 44.44 | 3 | 2 | 7 (installed 2016) | 100 | [5 empty] | UUG0635
United Utilities | SAVICK BROOK PUMPING STATION | Savick Brook PS (339CT) | 01PRE0083 | PRE0083 | SO | Storm discharge at pumping station | SD5031030990 | GB112071065470 | Savick Brook | SAVICK BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 416.93 | 49 | 53.8 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0636
United Utilities | LIGHTFOOT LANE PS | Lightfoot Lane PS | 01PRE0081 | PRE0081 | SO | Storm discharge at pumping station | SD5115033320 | GB112072065760 | Woodplumpton Brook | UNAMED TRIB WOODPLUMPTON BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0637
United Utilities | Haslam Park North and South Combined Sewer Overflow (Site ID 33026) (PRE0090) | Haslam Park North and South Combined Sewer Overflow (Site ID 33026) (PRE0090) | 17190870 | PRE0090 | SO | SO on sewer network | SD5140031170 | GB112071065470 | Savick Brook | SAVICK BROOK | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 0 | 0 | 9.7143 | 7 (installed 2016) | 99.99 | [5 empty] | UUG0638
United Utilities | Haslam Park North and South Combined Sewer Overflow (Site ID 33026) (PRE0090) | Haslam Park North and South Combined Sewer Overflow (Site ID 33026) (PRE0090) | 17190870 | PRE0090 | SO | SO on sewer network | SD5140031170 | GB112071065470 | Savick Brook | SAVICK BROOK | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 265.73 | 23 | 3.2857 | 7 (installed 2016) | 99.99 | [5 empty] | UUG0639
United Utilities | ST ANDREWS ROAD/ST MICHAEL CSO | St Andrew's Road/St Michael's Road CSO | 01SEF0012 | SEF0012 | SO | SO on sewer network | SD2955001654 | 348 |  | MERSEY ESTUARY | N/A | Formby | Not Applicable | Commissioned in 2016 - full year data expected | 211.03 | 78 | 66.8571 | 7 (installed 2016) | 99.73 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0640
United Utilities | ST MICHAELS ROAD/MANOR ROAD CSO | St Michaels Road/Manor Road CSO | 01SEF0013 | SEF0013 | SO | SO on sewer network | SD2955001655 | 348 |  | RIVER ALT (TIDAL) | N/A | Formby | Not Applicable | Commissioned in 2016 - full year data expected | 738.57 | 124 | 109.8571 | 7 (installed 2016) | 99.46 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0641
United Utilities | OS 49 ST ANDREWS ROAD CSO 38028 | Outside 49 St Andrews Road CSO | 016982650 | SEF0095 | SO | SO on sewer network | SD3079901011 | 172 |  | RIVER MERSEY ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 747.13 | 114 | 91.6 | 5 (installed 2018) | 99.45 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0642
United Utilities | OPPOSITE 53 MOOR LANE CSO 382G6 | Opposite 53 Moor Lane (in roundabout) Combined Sewer Overflow (Site ID 382G6) (SEF0097) | 016982750 | SEF0097 | SO | SO on sewer network | SJ3050098905 | 348 |  | RIVER MERSEY ESTUARY | N/A | Wallasey | Not Applicable | Commissioned in 2017 - full year data expected | 365.7 | 132 | 127 | 6 (installed 2017) | 98.24 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0643
United Utilities | O/S51 MOORLAND AVE CSO 382G6 | O/s 51 Moorland Avenue | 016982751 | SEF0098 | SO | SO on sewer network | SJ3050098904 | 348 |  | RIVER MERSEY ESTUARY | N/A | Wallasey | Not Applicable | Commissioned in 2017 - full year data expected | 290.6 | 114 | 103.5 | 6 (installed 2017) | 98.09 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0644
United Utilities | THE BYPASS/LPOOL RD JUNCT CSO 382UR | The Bypass / Liverpool Road Junction CSO | 016982752 | SEF0099 | SO | SO on sewer network | SJ3050098906 | 348 |  | RIVER MERSEY ESTUARY | N/A | Wallasey | Not Applicable | Commissioned in 2017 - full year data expected | 364.53 | 96 | 35.8333 | 6 (installed 2017) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0645
United Utilities | O/S 107 LIVERPOOL ROAD CSO 382D3 | O/S 107 Liverpool Road in Footpath CSO | 016982753 | SEF0100 | SO | SO on sewer network | SJ3050098902 | 348 |  | RIVER MERSEY ESTUARY | N/A | Wallasey | Not Applicable | Commissioned in 2017 - full year data expected | 33.53 | 30 | 29.3333 | 6 (installed 2017) | 97.74 | [5 empty] | UUG0646
United Utilities | BANKSFIELD AVENUE CSO 33027 | Banksfield Avenue CSO | 017180625 | PRE0114 | SO | SO on sewer network | SD5203031250 | GB112071065470 | Savick Brook | SAVICK BRK TRIB OF RIBBLE EST | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 19.24 | 13 | 10.8 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0647
United Utilities | WATLING STREET ROAD CSO 33024 | Watling Street Road CSO | 017180630 | PRE0118 | SO | SO on sewer network | SD5488031380 | GB112071065470 | Savick Brook | EAVES BROOK TRIB SAVICK BROOK | N/A | St Annes | Not Applicable | Commissioned in 2018 - full year data expected | 122.55 | 11 | 10 | 5 (installed 2018) | 100 | [5 empty] | UUG0648
United Utilities | VICTORIA RD CSO 33023 | Victoria Road CSO | 017180628 | PRE0119 | SO | SO on sewer network | SD5343031340 | GB112069061452 | Savick Brook | EAVES BROOK | N/A | St Annes; St Annes North; Blackpool South; Blackpool Central; Blackpool North; Southport, Ainsdale | Not Applicable | Commissioned in 2018 - full year data expected | 258.65 | 85 | 75.2 | 5 (installed 2018) | 99.52 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0649
United Utilities | CLIFTON PUMPING STATION | Clifton Village PS | 017091534 | PRE0121 | SO | Storm discharge at pumping station | SD4679030010 | GB112071065670 | Dow Brook | SAVICK BROOK TRIBUTARY | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 32.87 | 39 | 59.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0650
United Utilities | OUTSIDE 16 CORONATION RD CSO 381PQ | O/S 16 Coronation Road | 016982754 | SEF0101 | SO | SO on sewer network | SJ3050098903 | 348 |  | RIVER MERSEY ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 8.83 | 17 | 17.3333 | 6 (installed 2017) | 100 | [5 empty] | UUG0651
United Utilities | SHAROE GREEN LANE CSO 33034 | Sharoe Green Lane combined sewer overflow (33034) (PRE0124) | EPRLP3329XW | PRE0124 | SO | SO on sewer network | SD5393032010 | GB112071065470 | Savick Brook | SAVICK BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 40.85 | 24 | 30 | 5 (installed 2018) | 100 | [5 empty] | UUG0652
United Utilities | COLLEGE ROAD ESHE ROAD CSO 38109 | College Road/Eshe Road | 016982755 | SEF0102 | SO | SO on sewer network | SJ3149099470 | 348 |  | RIVER MERSEY ESTUARY | N/A | Wallasey | Not Applicable | Commissioned in 2016 - full year data expected | 83.67 | 53 | 127.4286 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0653
United Utilities | HARBORD ROAD PS 99047 | Harbord Road Sewage Pumping Station (Site ID 99047 ) (SEF0103) | 016931010 | SEF0103 | SO | SO on sewer network | SJ3080097840 | 348 |  | LIVERPOOL BAY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 24.8 | 31 | 28.2857 | 7 (installed 2016) | 100 | [5 empty] | UUG0654
United Utilities | LONGRIDGE CSO 343FT | Longridge Combined Sewer Overflow | 017160117 | RIB0028 | SO | SO on sewer network | SD5950036100 | GB112071065470 | Savick Brook | SAVICK BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 34.23 | 29 | 25.6 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0655
United Utilities | RIMROSE BROOK CSO | Rimrose Brook CSO | 016931012 | SEF0105 | SO | SO on sewer network | SJ3180095800 | 167 |  | RIVER MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 4.18 | 21 | 19 | 7 (installed 2016) | 100 | [5 empty] | UUG0656
United Utilities | BOOTLE NORTHERN OPC CSO 99102 | Bootle Northern OPC Combined Sewer Overflow | 016931013 | SEF0106 | SO | SO on sewer network | SJ3210095600 | 167 |  | RIVER MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 3 | 18 | 17.2857 | 7 (installed 2016) | 100 | [5 empty] | UUG0657
United Utilities | HOLME ROAD COMBINED SEWER OVERFLOW | HOLME ROAD CSO | 017160301 | SRI0004 | SO | SO on sewer network | SD5168029290 | GB112073071050 | Holme Beck | RIVER RIBBLE | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 611.83 | 123 | 90.4286 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0658
United Utilities | STRAND ROAD STORM SEWER OVERFLOW | Strand Road CSO | 016931014 | SEF0107 | SO | SO on sewer network | SJ3250094300 | 167 |  | RIVER MERSEY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 12 | 9 | 6.8571 | 7 (installed 2016) | 99.46 | [5 empty] | UUG0659
United Utilities | PREESALL WWTW PREES | PREESALL WwTW | 017260071 | 17260071 | ST | Storm tank at WwTW | SD3481046870 | GB531207212200 | WYRE | WYRE ESTUARY | 113 Lune | Fleetwood | Not Applicable | Commissioned in 2017 - full year data expected | 1198.59 | 72 | 51 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0660
United Utilities | KNOTT END PUMPING STATION | Seeds Pumping Station (Site ID 52541) (WYR0035) | 017260103 | WYR0035 | SO | SO on sewer network | SD3458048370 | GB641211171000 | Morecambe Bay | RIVER WYRE ESTUARY | Morecambe Bay (Leven) | Fleetwood | Not Applicable | Commissioned in 2017 - full year data expected | 24.6 | 5 | 4.8333 | 6 (installed 2017) | 100 | [5 empty] | UUG0661
United Utilities | CEMETERY LANE PUMPING STATION | Cemetery Lane Pumping Station (52540) and Bridge Farm Combined Sewer Overflow (525QK) | EPRKB3498EP | WYR0040 | SO | Storm discharge at pumping station | SD3707046030 | GB112069061451 | Wyre (Tidal) | UNKNOWN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 96.03 | 38 | 31.6 | 5 (installed 2018) | 89.1 | Comms failure / issue | Resolved - January after reporting year |  |  |  | UUG0662
United Utilities | Millers Bridge CSO | Millers Bridge CSO | 16931015 | SEF0108 | SO | SO on sewer network | SJ3293094400 | 167 |  | RIVER MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 0.08 | 1 | 2.8571 | 7 (installed 2016) | 100 | [5 empty] | UUG0663
United Utilities | PILLING LANE PS | Pilling Lane Pumping Station (Site ID PILLL) (WYR0073) | 017290557 | WYR0073 | SO | Storm discharge at pumping station | SD3607048950 | GB641211171000 | Morecambe Bay | RIVER WYRE ESTUARY | N/A | Fleetwood; Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 3.78 | 11 | 19.1667 | 6 (installed 2017) | 94.46 | [5 empty] | UUG0664
United Utilities | POOLEY BRIDGE EAST WWTW | Pooley Bridge East wastewater treatment works (Site ID POOLE) (017670085) | 017670085 | 17670085 | SO | Inlet SO at WwTW | NY4717024720 | GB102076071020 | Eamont (Upper) | RIVER EAMONT | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 0.24 | 3 | 2.8571 | 7 (installed 2016) | 99.94 | [5 empty] | UUG0665
United Utilities | POOLEY BRIDGE PUMPING STATION | Pooley Bridge SSO | 017680473 | EDE0060 | SO | SO on sewer network | NY4698024440 | GB102076071020 | Eamont (Upper) | RIVER EAMONT | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 196.73 | 48 | 50.4286 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0666
United Utilities | PLUMPTON NORTH WWTW PLUMN | PLUMPTON NORTH WwTW | 017670110 | 17670110 | SO | Inlet SO at WwTW | NY4910037520 | GB102076073991 | Petteril d/s M6 | RIVER PETTERIL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 164.25 | 16 | 43.8 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0667
United Utilities | PLUMLEY STW | PLUMLEY WwTW | 016810103 | 16810103 | SO | Inlet SO at WwTW | SJ7171075190 | GB112068060390 | Peover Eye | PEOVER EYE (VIA TRIB) | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 30.5 | 27 | 41 | 3 (installed 2020) | 99.64 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0668
United Utilities | PLUMBLAND WWTW | Plumbland WwTW | 017570072 | 17570072 | ST | Storm tank at WwTW | NY1394040300 | GB112075073640 | Ellen (lower) | RIVER ELLEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 4763.18 | 307 | 306.8 | 5 (installed 2018) | 52.44 | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0669
United Utilities | PICA STW | PICA WwTW | 017470038 | 17470038 | ST | Storm tank at WwTW | NY0232022860 | GB112074070040 | Lowca Beck | DYAN BECK | N/A | N/A | Not Applicable | Commissioned in 2021 - full year data expected | 114.53 | 40 | 58.5 | 2 (installed 2021) | 100 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0670
United Utilities | PENRITH WWTW (PENRT) | PENRITH WwTW | 017670084 | 17670084 | ST | Storm tank at WwTW | NY5525029570 | GB102076070990 | Eamont (Lower) | RIVER EAMONT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 480.95 | 21 | 35 | 4 (installed 2019) | 100 | [5 empty] | UUG0671
United Utilities | JUNCTION OF WORDSOWRTH STREET CSO | Junction of Wordsworth Street CSO | 01EDE0029 | EDE0029 | SO | SO on sewer network | NY5142030380 | GB102076071020 | Eamont (Upper) | THACKA BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.13 | 5 | 3.75 | 4 (installed 2019) | 99.97 | [5 empty] | UUG0672
United Utilities | SANDGATE (PENRITH) CSO (17552) | Sandgate (Penrith) CSO | 01EDE0033 | EDE0033 | SO | SO on sewer network | NY5169030290 | GB102076071020 | Eamont (Upper) | THACKA BECK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 10.57 | 22 | 14 | 3 (installed 2020) | 99.46 | [5 empty] | UUG0673
United Utilities | ARTHUR ST/MEETING HOUSE LANE CSO | Arthur Street/Meeting House Lane CSO | 017680535 | EDE0030 | SO | SO on sewer network | NY5151030290 | GB102076071020 | Eamont (Upper) | THACKA BECK CLVRT VIA A SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.03 | 1 | 23 | 4 (installed 2019) | 100 | [5 empty] | UUG0674
United Utilities | CASTLE DRIVE CSO | Castle Hill Drive CSO | 01EDE0035 | EDE0035 | SO | SO on sewer network | NY5188029731 | GB102076071020 | Eamont (Upper) | DOG BECK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 100 | [5 empty] | UUG0675
United Utilities | STAINTON (SNUFF MILL) SSO | Stainton SSO | 017680275 | EDE0080 | SO | SO on sewer network | NY4906027430 | GB102076071020 | Eamont (Upper) | RIVER EAMONT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1010.65 | 71 | 74.5 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0676
United Utilities | PENRITH OUTFALL CSO | Penrith Outfall CSO | 017680281 | EDE0081 | SO | SO on sewer network | NY5417029470 | GB102076070990 | Eamont (Lower) | RIVER EAMONT | N/A | N/A | Not Applicable | Dec 2023 | 9.43 | 4 |  | <1 yr (installed 2023) | 99.2701 | [5 empty] | UUG0677
United Utilities | BROUGHAM PUMPING STATION | Brougham Pumping Station (17502) (EDE0085) | 017680334 | EDE0085 | SO | Storm discharge at pumping station | NY5317028700 | GB102076071010 | Lowther (Lower) | TRIB RIVER EAMONT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 5 (installed 2018) | 100 | [5 empty] | UUG0678
United Utilities | NEWTON REIGNY PUMPING STATION | Newton Reigny PS | NPSWQD002805 | EDE0115 | SO | Storm discharge at pumping station | NY4791031890 | GB102076073992 | Petteril u/s M6 | RIVER PETTERIL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 666.75 | 64 | 44.3333 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0679
United Utilities | CARLETON HALL TEMPLEBANK CSO | Carleton Hall Templebank CSO | NPSWQD002845 | EDE0116 | SO | SO on sewer network | NY5306029380 | GB102076071020 | Eamont (Upper) | UNNAMED CULVERT OF EAMONTRIVER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1024.8 | 124 | 119 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0680
United Utilities | PENRITH SPS | Gillwilly PS | 017670039 | EDE0119 | SO | Storm discharge at pumping station | NY5082030500 | GB102076071020 | Eamont (Upper) | THACKA BECK | N/A | N/A | Not Applicable | Dec 2023 | 0 | 0 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0681
United Utilities | PARTINGTON WWTW | PARTINGTON WwTW | 016940148 | 16940148 | ST | Storm tank at WwTW | SJ7052090860 | GB112069060980 | Sinderland Brook | RED BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 695.36 | 70 | 55.75 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0682
United Utilities | LOCK LANE PARTINGTON CSO | Lock Lane CSO | 01TRA0035 | TRA0035 | SO | SO on sewer network | SJ7088091511 | GB112069061011 | Mersey/ Manchester Ship Canal (Irwell/Manchester Ship Canal to B | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1684.93 | 193 | 192.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0683
United Utilities | PARK ROAD (STRETFORD) CSO | Birch Road CSO | EPRSB3398EX | TRA0046 | SO | SO on sewer network | SJ7088091510 | GB112069061011 | Mersey/ Manchester Ship Canal (Irwell/Manchester Ship Canal to B | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 255.67 | 110 | 106.6667 | 3 (installed 2020) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0684
United Utilities | PARKGATE FARM (WARBURTON) CSO | Parkgate Farm Warburton CSO | EPRSB3398VQ | TRA0050 | SO | SO on sewer network | SJ6989089800 | GB112069061011 | Mersey/ Manchester Ship Canal (Irwell/Manchester Ship Canal to B | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 41.1 | 38 | 78.3333 | 3 (installed 2020) | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0685
United Utilities | PARDSHAW STW | PARDSHAW WwTW | 017570049 | 17570049 | ST | Storm tank at WwTW | NY0990024680 | GB112075070540 | Marron | BLACK BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 58.47 | 47 | 54.3333 | 3 (installed 2020) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0686
United Utilities | OVER KELLET WWTW | OVER KELLET WwTW | 017370075 | 17370075 | ST | Storm tank at WwTW | SD5164070240 | GB112073064430 | Keer - Lower | TRIB RIVER KEER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2700.99 | 156 | 150.2 | 5 (installed 2018) | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0687
United Utilities | ORTON STW | ORTON WwTW | 017270008 | 17270008 | SO | Inlet SO at WwTW | NY6291007680 | GB112072071800 | Chapel Beck | CHAPEL BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1328.35 | 103 | 114.6667 | 3 (installed 2020) | 99.15 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0688
United Utilities | ORTON STW | ORTON WwTW | 017270008 | 17270008 | ST | Storm tank at WwTW | NY6291007680 | GB112072071800 | Chapel Beck | CHAPEL BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 3320.41 | 174 | 146.3333 | 3 (installed 2020) | 99.96 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0689
United Utilities | OLDHAM WWTW | OLDHAM WwTW | 016950038 | 16950038 | ST | Storm tank at WwTW | SD8937004430 | GB112069061120 | Wince Brook | WINCE BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 99.86 | [5 empty] | UUG0690
United Utilities | OLDHAM WWTW | OLDHAM WwTW | 016950038 | 16950038 | SO | Inlet SO at WwTW | SD8937004430 | GB112069061120 | Wince Brook | WINCE BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 100 | [5 empty] | UUG0691
United Utilities | OLDHAM WWTW | OLDHAM WwTW | 016950038 | 16950038 | ST | Storm tank at WwTW | SD8937004430 | GB112069061120 | Wince Brook | WINCE BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 11.53 | 2 | 0.66667 | 3 (installed 2020) | 100 | [5 empty] | UUG0692
United Utilities | OLDHAM WWTW | OLDHAM WwTW | 016950038 | 16950038 | ST | Storm tank at WwTW | SD8937004430 | GB112069061120 | Wince Brook | WINCE BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1021.38 | 86 | 99 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0693
United Utilities | SHEEPFOOT LANE CSO | SHEEPFOOT LANE CSO | 01OLD0032 | OLD0032 | SO | SO on sewer network | SD9063006911 | GB112069061161 | Irk (Sourtce to Wince Brook) | PLUMPTON CLOUGH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 29.7 | 49 | 56.25 | 4 (installed 2019) | 98.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0694
United Utilities | BOUNDARY PARK ROAD CSO | BOUNDARY PARK ROAD CSO | 01OLD0033 | OLD0033 | SO | SO on sewer network | SD9063006910 | GB112069061161 | Irk (Sourtce to Wince Brook) | PLUMPTON CLOUGH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.33 | 10 | 12 | 4 (installed 2019) | 100 | [5 empty] | UUG0695
United Utilities | WESTHULME HOSPITAL CSO | Westhulme Hospital CSO | 01OLD0034 | OLD0034 | SO | SO on sewer network | SD9063006030 | GB112069061161 | Irk (Sourtce to Wince Brook) | PLUMPTON CLOUGH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 6.03 | 14 | 31.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0696
United Utilities | STONELEIGH PARK CSO | STONELEIGH PARK CSO | 01OLD0039 | OLD0039 | SO | SO on sewer network | SD9377006330 | GB112069064690 | Beal | RIVER BEAL VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 3.97 | 19 | 32.5 | 4 (installed 2019) | 100 | [5 empty] | UUG0697
United Utilities | SWAN MILL/DRUMMER MILL CSO | Swan Mill CSO | 016983314 | OLD0042 | SO | SO on sewer network | SD8896004570 | GB112069061120 | Wince Brook | SPRINGS BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 365.49 | 121 | 105.75 | 4 (installed 2019) | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0698
United Utilities | SUFFOLK ST COMBINED SEWER OVERFLOW | Suffolk Street CSO | 016983311 | OLD0037 | SO | SO on sewer network | SD9084003810 | GB112069061120 | Wince Brook | BOWER BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0 | 4 (installed 2019) | 100 | [5 empty] | UUG0699
United Utilities | HOLLINWOOD CEMETERY CSO | Hollinwood Cemetry CSO | 01OLD0074 | OLD0074 | SO | SO on sewer network | SD9116001881 | GB112069061152 | Medlock (Lumb Brook to Irwell) | LORDS BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 8.67 | 10 | 27.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0700
United Utilities | LIMESIDE ROAD/FOX MILL CSO | Limeside Road/Fox Mill CSO | 01OLD0075 | OLD0075 | SO | SO on sewer network | SD9116001882 | GB112069061152 | Medlock (Lumb Brook to Irwell) | MOSTON BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 16.27 | 28 | 9.75 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0701
United Utilities | SNIPE CLOUGH CSO | Snipe Clough CSO | 016982237 | OLD0100 | SO | SO on sewer network | SD9374903315 | GB112069061151 | Medlock (Source to Lumb Brook) | GLODWICK BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 112.8 | 31 | 47.75 | 4 (installed 2019) | 85.73 | Comms failure / issue | Resolved - January after reporting year | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0702
United Utilities | COAL PIT LANE CSO | Coal Pit Lane CSO | 016950431 | OLD0102 | SO | SO on sewer network | SD9287101151 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER MEDLOCK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 19.03 | 21 | 19.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0703
United Utilities | FERNEYFIELD ROAD CSO OLD0104 | Ferneyfield Road Sewer | 016950498 | OLD0104 | SO | SO on sewer network | SD8976505556 | GB112069061120 | Wince Brook | SPRING BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.33 | 3 | 5.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0704
United Utilities | HUNT LANE COMBINED SEWER OVERFLOW | Hunt Lane CSO | 016950499 | OLD0105 | SO | SO on sewer network | SD9057004990 | GB112069061120 | Wince Brook | STOCK BROOK CULVERT VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 29.03 | 9 | 24.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0705
United Utilities | S. CHADDERTON/ | South Chadderton / The Causeway Oldham CSO | 016950546 | OLD0106 | SO | SO on sewer network | SD8908004340 | GB112069061120 | Wince Brook | WINCE BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 280.54 | 74 | 60 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0706
United Utilities | HATHERSHAW CSO | Hathershaw Playing Field | 016952063 | OLD0109 | SO | SO on sewer network | SD9288001150 | GB112069061151 | Medlock (Source to Lumb Brook) | RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 16.47 | 2 | 10.3333 | 3 (installed 2020) | 99.98 | [5 empty] | UUG0707
United Utilities | WOODBROOK ROAD CSO | Woodbrook Road CSO | 01OLD0113 | OLD0113 | SO | SO on sewer network | SD9671005270 | GB112069061151 | Medlock (Source to Lumb Brook) | WOOD BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 1.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0708
United Utilities | 250M OF ASHTON ROAD BARDSLEY PS CSO | 250 metres d/s Ashton Road (Bardsley PS) CSO | 016980030 | OLD0120 | SO | Storm discharge at pumping station | SD9287001150 | GB112069061151 | Medlock (Source to Lumb Brook) | RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 145.09 | 52 | 99.75 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0709
United Utilities | THE CAUSEWAY CHADDERTON WWNPS | The Causeway (Chadderton) Wastewater Network Pumping Station | 016983315 | OLD0121 | SO | Storm discharge at pumping station | SD8910004470 | GB112069061120 | Wince Brook | WINCE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 134.1 | 55 | 57.5 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0710
United Utilities | ALFORD STREET PUMPING STATION | Alford Street PS | 016982210 | OLD0123 | SO | Storm discharge at pumping station | SD9018002570 | GB112069061152 | Medlock (Lumb Brook to Irwell) | MOSTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 5 (installed 2018) | 97.27 | [5 empty] | UUG0711
United Utilities | GREENGATE COMBINED SEWER OVERFLOW | Greengate CSO | 016982738 | OLD0128 | SO | SO on sewer network | SD8847004800 | GB112069061120 | Wince Brook | WINCE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 48.4 | 50 | 40.75 | 4 (installed 2019) | 98.91 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0712
United Utilities | LIMESIDE RD/CHURCH CSO | Limeside Road CSO | 016982632 | OLD0132 | SO | SO on sewer network | SD9116001880 | GB112069061152 | Medlock (Lumb Brook to Irwell) | LORDS BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.17 | 5 | 3.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0713
United Utilities | ARKWRIGHT STREET CSO | Arkwright Street CSO | 016982739 | OLD0136 | SO | SO on sewer network | SD9117004990 | GB112069061120 | Wince Brook | STOCK BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 29.62 | 50 | 46 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0714
United Utilities | ABBEYHILLS COMBINED SEWER OVERFLOW | Abbeyhills Combined Sewer Overflow (31028) (OLD0124) | 01OLD0124 | OLD0124 | SO | SO on sewer network | SD9482203177 | GB112069061151 | Medlock (Source to Lumb Brook) | CULVERT GLODWICK BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0.8 | 5 (installed 2018) | 96.34 | [5 empty] | UUG0715
United Utilities | ABBEYHILLS COMBINED SEWER OVERFLOW | Abbeyhills Road CSO | 016982467 | OLD0151 | SO | SO on sewer network | SD9482203177 | GB112069061151 | Medlock (Source to Lumb Brook) | TRIB RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0.33333 | 3 (installed 2020) | 99.99 | [5 empty] | UUG0716
United Utilities | MOSTON RD/ CHADDERTON LOW LEVEL PS | Moston Road Combined Sewer Overflow/Chadderton Low Level Pumping Station (318N4) (OLD0157) | 016983361 | OLD0157 | SO | Storm discharge at pumping station | SD8869004570 | GB112069061120 | Wince Brook | WINCE BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 45.23 | 39 | 44.2 | 5 (installed 2018) | 98.73 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0717
United Utilities | FOXDENTON LANE CSO | Foxdenton Lane CSO | 016983136 | OLD0163 | SO | SO on sewer network | SD8957004540 | GB112069061120 | Wince Brook | WINCE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 112.9 | 93 | 84.5 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0718
United Utilities | 674 RIPPONDEN ROAD CSO | Ripponden Road CSO | 016983139 | OLD0165 | SO | SO on sewer network | SD9507407373 | GB112069064690 | Beal | CLVRT'D SECTION HODGE CLOUGH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 70.42 | 36 | 23 | 4 (installed 2019) | 100 | [5 empty] | UUG0719
United Utilities | NORTHWICH WWTW | NORTHWICH WwTW | 016810099 | 16810099 | SO | Inlet SO at WwTW | SJ6374074160 | GB112068060500 | Weaver (Dane to Frodsham) | RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 24.24 | 12 | 9 | 3 (installed 2020) | 98.9 | [5 empty] | UUG0720
United Utilities | NORTHWICH WWTW | NORTHWICH WwTW | 016810099 | 16810099 | ST | Storm tank at WwTW | SJ6374074160 | GB112068060500 | Weaver (Dane to Frodsham) | RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1128.38 | 90 | 107.3333 | 3 (installed 2020) | 46.75 | Sensor failure / issue | Resolved - Dec | Data collection - EDM non-representative location | Resolved - Dec | Other investigation - non-WINEP/Green Recovery | UUG0721
United Utilities | OAKMERE PUMPING STATION | Oakmere Pumping Station | EPRMB3297NU | CRE0088 | SO | Storm discharge at pumping station | SJ5683568945 | GB112068060480 | Cuddington Brook (Source to Crowton Brook) | FIR BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 369.68 | 37 | 28.6667 | 3 (installed 2020) | 81.41 | Sensor failure / issue | Resolved - Aug |  |  |  | UUG0722
United Utilities | CUDDINGTON PUMPING STATION | Cuddington Pumping Station | EPRMB3297AV | CRE0087 | SO | Storm discharge at pumping station | SJ5986072515 | GB112068060480 | Cuddington Brook (Source to Crowton Brook) | CUDDINGTON (CLIFFE) BROOKE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 100 | [5 empty] | UUG0723
United Utilities | CHESTER WAY | Northwich Resewerage Scheme | 01VRY0001 | VRY0001 | SO | SO on sewer network | SJ6593773780 | GB112068060470 | Dane (Wheelock to Weaver) | River Dane | N/A | N/A | Not Applicable | Dec 2023 | 2065.3 | 208 |  | <1 yr (installed 2023) | 97.3913 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0724
United Utilities | ANDERTON FIELD NO28 | Anderton Field No. 28 | 01VRY0002 | VRY0002 | SO | Storm discharge at pumping station | SJ6496076140 | GB112068060510 | Cogshall Brook | Marbury Brook | N/A | N/A | Not Applicable | Dec 2023 | 14.33 | 32 |  | <1 yr (installed 2023) | 65.9341 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0725
United Utilities | MERE HEATH PUMPING STATION | Mere Heath PS | 016881958 | VRY0018 | SO | Storm discharge at pumping station | SJ6659069880 | GB112068060470 | Dane (Wheelock to Weaver) | PECKMILL BK (TRIB OF R.DANE) | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 4.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG0726
United Utilities | 310-314 CHESTER ROAD CSO | 310 -314 Chester Road CSO | 016810821 | VRY0020 | SO | SO on sewer network | SJ6209072650 | GB112068060480 | Cuddington Brook (Source to Crowton Brook) | HANDFORTH BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 81.87 | 20 | 13.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0727
United Utilities | DOCK ROAD SPS | Dock Road Sewage PS | 016810823 | VRY0021 | SO | Storm discharge at pumping station | SJ6568073230 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | Not Applicable | Dec 2023 | 0.66 | 1 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0728
United Utilities | REAR 237 RUNCORN ROAD CSO (472PR) | Rear 237 Runcorn Road CSO | 01VRY0051 | VRY0051 | SO | SO on sewer network | SJ6292075180 | GB112068060510 | Cogshall Brook | TRENT AND MERSEY CANAL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 55.23 | 48 | 68.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0729
United Utilities | WOODLANDS GROVE CSO | Woodlands Grove CSO | 01VRY0052 | VRY0052 | SO | SO on sewer network | SJ6282075520 | GB112068060510 | Cogshall Brook | TRIB OF TRENT & MERSEY CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 7.8 | 20 | 41 | 5 (installed 2018) | 96.09 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0730
United Utilities | CUDDINGTON LANE CSO (471QL) | Cuddington Lane (adjacent Pipe Bridge) CSO | 01VRY0053 | VRY0053 | SO | SO on sewer network | SJ5990072500 | GB112068060480 | Cuddington Brook (Source to Crowton Brook) | CUDDINGTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 21.97 | 26 | 25.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG0731
United Utilities | CUDDINGTON LANE CSO (471QL) | Cuddington Lane (Woods) CSO | 01VRY0054 | VRY0054 | SO | SO on sewer network | SJ5990072500 | GB112068060480 | Cuddington Brook (Source to Crowton Brook) | CUDDINGTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 127.5 | 26 | 8.6667 | 3 (installed 2020) | 99.99 | [5 empty] | UUG0732
United Utilities | WASTE LANE CSO SITE ID 472W0 | WASTE LANE CSO | 01VRY0055 | VRY0055 | SO | SO on sewer network | SJ5944071600 | GB112068060480 | Cuddington Brook (Source to Crowton Brook) | CUDDINGTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 32.93 | 22 | 13 | 3 (installed 2020) | 100 | [5 empty] | UUG0733
United Utilities | OUTSIDE 51 CHURCH STREET CSO 471JC | Outside 51 Church Street (Davenham) CSO | 016892455 | VRY0056 | SO | SO on sewer network | SJ6644171121 | GB112068060470 | Dane (Wheelock to Weaver) | ELDERSBRIAR BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 111.3 | 67 | 95.3333 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0734
United Utilities | OFF SCHOOL LANE CSO (472JI) | Off School Lane CSO | 01VRY0060 | VRY0060 | SO | SO on sewer network | SJ6489071570 | GB112068060460 | Weaver (Marbury Brook to Dane) | WEAVER NAVIGATION | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 99.99 | [5 empty] | UUG0735
United Utilities | SCHOOL LANE/LODGE LANE CSO | School Lane/Lodge Lane CSO | 01VRY0061 | VRY0061 | SO | SO on sewer network | SJ6473071330 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0736
United Utilities | OFF JACK LANE | Jack Lane CSO | 01VRY0066 | VRY0066 | SO | SO on sewer network | SJ6610069200 | GB112068060470 | Dane (Wheelock to Weaver) | TRIB OF PECKMILL BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.4 | 3 | 4.3333 | 3 (installed 2020) | 97.9 | [5 empty] | UUG0737
United Utilities | SPENCER STREET/DARWIN STREET CSO | SPENCER STREET / DARWIN STREET CSO | 01VRY0067 | VRY0067 | SO | SO on sewer network | SJ6559073060 | GB112068060460 | Weaver (Marbury Brook to Dane) | WEAVER NAVIGATION VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1.73 | 9 | 10.6667 | 3 (installed 2020) | 99.99 | [5 empty] | UUG0738
United Utilities | NAVIGATION ROAD CSO (472HN) | Navigation Road (Northwich) CSO | 01VRY0068 | VRY0068 | SO | SO on sewer network | SJ6557073230 | GB112068060460 | Weaver (Marbury Brook to Dane) | WEAVER NAVIGATION | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 79.63 | 88 | 79.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0739
United Utilities | GREENBANK LANE CSO NORTHWICH | Greenbank Lane CSO Northwich | 016892403 | VRY0073 | SO | SO on sewer network | SJ6510072320 | GB112068060460 | Weaver (Marbury Brook to Dane) | THE RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 146.07 | 62 | 50.1667 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0740
United Utilities | 230 LONDON ROAD CSO | 230 London Road CSO | 01VRY0074 | VRY0074 | SO | SO on sewer network | SJ6598073260 | GB112068060470 | Dane (Wheelock to Weaver) | RIVER DANE VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 12.57 | 29 | 28.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0741
United Utilities | WINNINGTON STREET CSO 472YM | Winnington Street CSO | 01VRY0077 | VRY0077 | SO | SO on sewer network | SJ6567073870 | GB112068060500 | Weaver (Dane to Frodsham) | RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2.37 | 12 | 23.8 | 5 (installed 2018) | 100 | [5 empty] | UUG0742
United Utilities | MANORA ROAD (DANE NURSERIES) CSO | Manora Road (Dane Nurseries) CSO | 016881776 | VRY0078 | SO | SO on sewer network | SJ6613073480 | GB112068060470 | Dane (Wheelock to Weaver) | RIVER DANE | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 64.37 | 70 | 73 | 4 (installed 2019) | 99.99 |  |  | Data collection - EDM non-representative location | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0743
United Utilities | OFF CARLTON ROAD CSO | Off Carlton Road CSO | EPRSB3398WP | VRY0079 | SO | SO on sewer network | SJ6626073120 | GB112068060470 | Dane (Wheelock to Weaver) | RIVER DANE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 41.97 | 54 | 62.3333 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0744
United Utilities | MARLOWE ROAD (PLAYING FIELDS) CSO | Marlowe Road (Playing Fields) CSO | 01VRY0080 | VRY0080 | SO | SO on sewer network | SJ6704072970 | GB112068060470 | Dane (Wheelock to Weaver) | RIVER DANE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 284.1 | 92 | 80.6667 | 3 (installed 2020) | 99.68 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0745
United Utilities | 102 MIDDLEWICH ROAD CSO | 102 Middlewich Road CSO | 016892222 | VRY0091 | SO | SO on sewer network | SJ6753073600 | GB112068060370 | Wade Brook | TRIB OF WADE BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 250.43 | 98 | 88.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0746
United Utilities | O/S 173 MIDDLEWICH RD | XXX Middlewich Road CSO | 01VRY0092 | VRY0092 | SO | SO on sewer network | SJ6753073601 | GB112068060370 | Wade Brook | WADE BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.33 | 1 | 2.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0747
United Utilities | O/S 49 EDWARD ST | Edward Street (Northwich) CSO | 01VRY0093 | VRY0093 | SO | SO on sewer network | SJ6753073602 | GB112068060370 | Wade Brook | WADE BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.33 | 1 | 3.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0748
United Utilities | MIDDLEWICH RD/PARKFIELD RD CSO | Middlewich Road/Parkfield Road CSO | 016892279 | VRY0094 | SO | SO on sewer network | SJ6697079240 | GB112068060420 | Arley Brook (Source to Gale Brook) | RIVER DANE VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 96.67 | 73 | 74 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0749
United Utilities | REAR OF 36 PETER STREET | Alleyway Adjacent to Rear of Peter Street CSO | 01VRY0095 | VRY0095 | SO | SO on sewer network | SJ6679074220 | GB112068060370 | Wade Brook | WADE BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 4 | 3 (installed 2020) | 100 | [5 empty] | UUG0750
United Utilities | OLLERSHAW LANE WW NTWK PS | Ollershaw Lane PS | 01VRY0099 | VRY0099 | SO | Storm discharge at pumping station | SJ6719975770 | GB112068060390 | Peover Eye | Newman’s Flash leading to Witton Brook | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 529.86 | 48 | 17 | 3 (installed 2020) | 100 |  |  | Data collection - EDM non-representative location | Scheduled |  | UUG0751
United Utilities | WEIR STREET COMBINED SEWER OVERFLOW | WEIR STREET CSO | 01VRY0102 | VRY0102 | SO | SO on sewer network | SJ6567073230 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0752
United Utilities | CASTLE ST | Castle Street, Northwich | 01VRY0103 | VRY0103 | SO | SO on sewer network | SJ6567073680 | GB112068060460 | Weaver (Marbury Brook to Dane) | River Weaver | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0753
United Utilities | CHURCH STREET CSO | Church Street CSO | 01VRY0104 | VRY0104 | SO | SO on sewer network | SJ6631071100 | GB112068060470 | Dane (Wheelock to Weaver) | ELDERSBRIAR BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 1.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG0754
United Utilities | REAR MEADOW LANE CSO | Rear of XX Meadow Lane CSO | 01VRY0106 | VRY0106 | SO | SO on sewer network | SJ6611069210 | GB112068060470 | Dane (Wheelock to Weaver) | TRIB PECKMILL BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 1 | 3 (installed 2020) | 99.53 | [5 empty] | UUG0755
United Utilities | MANCHESTER ROAD (LOSTOCK) CSO | Manchester Road (Lostock) CSO | EPRSB3399DG | VRY0116 | SO | SO on sewer network | SJ6855074780 | GB112068060390 | Peover Eye | WINCHAM BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0.66667 | 3 (installed 2020) | 100 | [5 empty] | UUG0756
United Utilities | BARONS QUAY PS | Barons Quay PS | 01VRY0118 | VRY0118 | SO | Storm discharge at pumping station | SJ6581074270 | GB112068060500 | Weaver (Dane to Frodsham) | River Weaver | N/A | N/A | Not Applicable | Dec 2023 | 0 | 0 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0757
United Utilities | COMBERBACH PS | Comberbach PS | 016810065 | VRY0128 | SO | Storm discharge at pumping station | SJ6499077140 | GB112068060400 | Forge (Kidd) Brook | KID (FORGE) BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 79.72 | 28 | 29.75 | 4 (installed 2019) | 99.83 | [5 empty] | UUG0758
United Utilities | POPLAR COTTAGES CSO | Poplar Cottages CSO | 016881722 | VRY0135 | SO | SO on sewer network | SJ6456077200 | GB112068060400 | Forge (Kidd) Brook | TRIB OF KID BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 10.87 | 7 | 6.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0759
United Utilities | 181 LONDON ROAD CSO | 181 London Road CSO | 016892203 | VRY0144 | SO | SO on sewer network | SJ6594072970 | GB112068060470 | Dane (Wheelock to Weaver) | RIVER DANE VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 85.63 | 84 | 81.3333 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0760
United Utilities | 42 RUNCORN ROAD CSO | 42 Runcorn Road CSO | 016892245 | VRY0147 | SO | SO on sewer network | SJ6375074630 | GB112068060500 | Weaver (Dane to Frodsham) | WEAVER NAVIGATION | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 63.83 | 37 | 35.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0761
United Utilities | NEWTON ARLOSH WWTW NEWTA | NEWTON ARLOSH WwTW | 017570196 | 17570196 | SO | Inlet SO at WwTW | NY1909055590 | GB530207614700 | SOLWAY | TRIB OF RIVER WAMPOOL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 500.11 | 98 | 130.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0762
United Utilities | 3-8 MORNINGSIDE CSO 3282GE | 3/8 Morningside CSO | 016983112 | SEF0118 | SO | SO on sewer network | SJ3332099130 | 348 |  | RIMROSE BROOK, TRIB RVR MERSEY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 2.53 | 7 | 6.8333 | 6 (installed 2017) | 91.23 | [5 empty] | UUG0763
United Utilities | NEWBIGGIN (LEVEN) WWTW NEWBG | NEWBIGGIN WwTW | 017370051 | 17370051 | ST | Storm tank at WwTW | SD2675168941 | GB112073071150 | Deep Meadows Beck | DEEP MEADOWS BECK | 129 Morecambe Bay | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 3927.24 | 223 | 166.1667 | 6 (installed 2017) | 99.95 |  |  | Performance - Infiltration | Scheduled | Other investigation - non-WINEP/Green Recovery | UUG0764
United Utilities | NEWBIGGIN (LEVEN) WWTW NEWBG | NEWBIGGIN WwTW | 017370051 | 17370051 | ST | Storm tank at WwTW | SD2638068970 | GB112073071150 | Deep Meadows Beck | DEEP MEADOWS BECK | 129 Morecambe Bay | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 10.9 | 12 | 15.3333 | 6 (installed 2017) | 99.95 | [5 empty] | UUG0765
United Utilities | BAYCLIFF PUMPING STATION 39051 | Baycliffe PS | 017370199 | LAK0001 | SO | Storm discharge at pumping station | SD2905071910 | GB641211171000 | Morecambe Bay | MORECAMBE BAY ESTURIANE WATERS | Morecambe Bay (Leven) | Walney West Shore | Not Applicable | Commissioned in 2016 - full year data expected | 1712.6 | 101 | 80.4286 | 7 (installed 2016) | 99.89 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP or Green Recovery | UUG0766
United Utilities | GLEASTON CASTLE CSO | Gleaston Castle CSO | 017480365 | LAK0053 | SO | SO on sewer network | SD2607072140 | GB112073071150 | Deep Meadows Beck | GLEASTON BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 4066.63 | 173 | 138 | 5 (installed 2018) | 100 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Stage 1c: Confirmed "hydraulic issue" | UUG0767
United Utilities | NETHER PEOVER STW | NETHER PEOVER WwTW | 016810098 | 16810098 | ST | Storm tank at WwTW | SJ7340573665 | GB112068060390 | Peover Eye | TRIB CROW BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 198.04 | 78 | 103.75 | 4 (installed 2019) | 99.81 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0768
United Utilities | HALEWOOD PUMPING STATION | Halewood Pumping Station (HALEW) (HAL0134) | 016983248 | HAL0134 | SO | Storm discharge at pumping station | SJ4860082800 | 167 |  | THE MERSEY ESTAURY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 8.96 | 8 | 5.75 | 4 (installed 2019) | 100 | [5 empty] | UUG0769
United Utilities | NEAR SAWREY WWTW NEARS | NEAR SAWREY WwTW | 017370030 | 17370030 | SO | Inlet SO at WwTW | SD3660095110 | GB112073071400 | Cunsey Beck/Black Beck | CUNSEY BECK | N/A | Windermere, Millerground Landing | Not Applicable | Commissioned in 2016 - full year data expected | 2028.02 | 104 | 126.7143 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0770
United Utilities | BEAM BRIDGE PUMPING STATION | Beam Bridge PS | 016810192 | CRE0022 | SO | Storm discharge at pumping station | SJ6515053560 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1123.88 | 96 | 100.75 | 4 (installed 2019) | 99.73 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0771
United Utilities | CLIFFORD AVENUE WW NTWK PS | Clifford Avenue CSO | 01SRI0041 | SRI0059 | SO | SO on sewer network | SD4813026380 | 175 |  | LONGTON BROOK | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 277.3 | 42 | 36.5714 | 7 (installed 2016) | 99.99 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0772
United Utilities | MURTON WASTEWATER TREATMENT WORKS | MURTON WwTW | 017680532 | 17680532 | SO | Inlet SO at WwTW | NY7234021670 | GB102076070850 | Trout Beck (Murton) | MURTON BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 15.06 | 46 | 59.5 | 4 (installed 2019) | 99.87 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0773
United Utilities | MURTON BRIDGE HOUSE PUMPING STATION | Murton (Bridge House) PS | 017680533 | EDE0114 | SO | Storm discharge at pumping station | NY7275121661 | GB102076070850 | Trout Beck (Murton) | MURTON BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 13.31 | 7 | 3.6 | 5 (installed 2018) | 91.89 | [5 empty] | UUG0774
United Utilities | MOTHERBY WASTEWATER TREATMENT WORKS | MOTHERBY WwTW | 017670105 | 17670105 | SO | Inlet SO at WwTW | NY4322028690 | GB102076073992 | Petteril u/s M6 | RIVER PETTERIL | N/A | N/A | Not Applicable | Dec 2023 | 19.27 | 10 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0775
United Utilities | PENRUDDOCK SPS | Penruddock Sewage PS | 017680293 | EDE0094 | SO | Storm discharge at pumping station | NY4293028190 | GB102076073992 | Petteril u/s M6 | TRIB RIVER PETTERIL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 96.13 | 63 | 51.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0776
United Utilities | MOSSLEY STW | MOSSLEY WwTW | 016940089 | 16940089 | SO | Inlet SO at WwTW | SD9732000880 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2059.04 | 119 | 111.5 | 4 (installed 2019) | 100 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Resolved - Sep | Other investigation - non-WINEP/Green Recovery | UUG0777
United Utilities | MOSSLEY STW | MOSSLEY WwTW | 016940089 | 16940089 | ST | Storm tank at WwTW | SD9732000880 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2348.23 | 202 | 242.25 | 4 (installed 2019) | 57.37 | Comms failure / issue | N/A - Ongoing investigation | Performance - Other maintenance / capital works (e.g. jetting) | Scheduled | Other investigation - non-WINEP/Green Recovery | UUG0778
United Utilities | ROACHES LOCK CSO | Roaches Lock | 016940369 | TAM0035 | SO | SO on sewer network | SD9796003130 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 36.13 | 46 | 36 | 3 (installed 2020) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0779
United Utilities | STOCKPORT ROAD CSO | Stockport Road CSO | 01TAM0086 | TAM0086 | SO | SO on sewer network | SD9705002570 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | COUNTY BROOK | N/A | N/A | Not Applicable | Dec 2023 | 363.73 | 62 |  | <1 yr (installed 2023) | 98.5507 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0780
United Utilities | STAMFORD ROAD CSO | STAMFORD ROAD CSO | 01TAM0087 | TAM0087 | SO | SO on sewer network | SD9716002650 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | COUNTY BROOK | N/A | N/A | Not Applicable | Dec 2023 | 1312.5 | 83 |  | <1 yr (installed 2023) | 99.0099 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0781
United Utilities | MANCHESTER ROAD CSO | Manchester Road CSO | 01TAM0088 | TAM0088 | SO | SO on sewer network | SD9740001660 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Not Applicable | Dec 2023 | 2257.7 | 198 |  | <1 yr (installed 2023) | 97.7273 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0782
United Utilities | DARK LANE CSO 441SH | DARK LANE CSO | 01TAM0089 | TAM0089 | SO | SO on sewer network | SD9765002610 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | UNNAMED TRIB RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 4.23 | 16 | 21.6 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0783
United Utilities | WAGGON ROAD CSO | WAGGON ROAD CSO | 01TAM0091 | TAM0091 | SO | SO on sewer network | SD9753001970 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.4 | 4 | 4.6 | 5 (installed 2018) | 100 | [5 empty] | UUG0784
United Utilities | MORLAND WASTEWATER TREATMENT WORKS | MORLAND WwTW | 017670019 | 17670019 | SO | Inlet SO at WwTW | NY5974022750 | GB102076070830 | Morland Beck | MORLAND BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 888.12 | 120 | 231.75 | 4 (installed 2019) | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0785
United Utilities | SCHOLA GREEN LANE PS | Schola Green Lane Pumping Station | 017370197 | LAN0109 | SO | Storm discharge at pumping station | SD4355063580 | GB112072065950 | Overton Dyke | MORECAMBE BAY | 115 Morecambe Bay East | Morecambe North; Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 33.1 | 13 | 14.8333 | 6 (installed 2017) | 100 | [5 empty] | UUG0786
United Utilities | MOBBERLEY WWTW | MOBBERLEY WwTW | 016910010 | 16910010 | SO | Inlet SO at WwTW | SJ7834080290 | GB112069061330 | Mobberley Brook | MOBBERLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 261 | 93 | 103 | 4 (installed 2019) | 99.96 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Scheduled | Stage 1c: Confirmed "hydraulic issue" | UUG0787
United Utilities | MOBBERLEY WWTW | MOBBERLEY WwTW | 016910010 | 16910010 | ST | Storm tank at WwTW | SJ7834080290 | GB112069061330 | Mobberley Brook | MOBBERLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1184.31 | 103 | 103.75 | 4 (installed 2019) | 96.94 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Scheduled | Stage 1c: Confirmed "hydraulic issue" | UUG0788
United Utilities | TOWN LANE CSO | Town Lane CSO | 016881767 | MAC0162 | SO | SO on sewer network | SJ7891079820 | GB112069061330 | Mobberley Brook | MOBBERLEY BROOK TRIB RV BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 634.6 | 105 | 132.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0789
United Utilities | THE GREENACRES CSO | The Greenacres CSO | 017180545 | SRI0060 | SO | SO on sewer network | SD4979027051 | 175 |  | UNNAMED TRIB. OF MILL BROOK | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 47.17 | 13 | 15.5714 | 7 (installed 2016) | 99.99 | [5 empty] | UUG0790
United Utilities | MILNTHORPE SEWAGE PS MLNTH | Milnthorpe Sewage PS | 017380339 | LAK0052 | SO | Storm discharge at pumping station | SD4939081400 | GB112073071070 | Bela | RIVER BELA | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1744.21 | 86 | 69.2 | 5 (installed 2018) | 98.82 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0791
United Utilities | HEVERSHAM SEWAGE PUMPING STATION | Heversham Sewage PS | 01LAK0055 | LAK0055 | SO | Storm discharge at pumping station | SD4864083090 | GB112073071070 | Bela | MARSH DRAIN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1474.38 | 125 | 88.4 | 5 (installed 2018) | 99.84 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG0792
United Utilities | CROFT DRV SHORE RD CSO CALDY 512RB | Croft Drive/Shore Road CSO | CG037860101 | WIR0093 | SO | SO on sewer network | SJ2223084820 | 166 |  | RIVER DEE ESTUARY | N/A | West Kirby | Not Applicable | Commissioned in 2016 - full year data expected | 900 | 37 | 16.4286 | 7 (installed 2016) | 56.86 | Comms failure / issue | Resolved - Jun |  |  | Other investigation - non-WINEP/Green Recovery | UUG0793
United Utilities | ASH MEADOW PUMPING STATION | Ash Meadow Pumping Station (Site id ASHME)(LAK0100) | 017380414 | LAK0100 | SO | Storm discharge at pumping station | SD4463178321 | GB531207312000 | KENT | THE KENT ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 242.7 | 27 | 20.1667 | 6 (installed 2017) | 100 | [5 empty] | UUG0794
United Utilities | HESKETH LANE CSO | HESKETH LANE CSO | 01WLN0019 | WLN0019 | SO | SO on sewer network | SD4569021050 | 175 |  | RIVER DOUGLAS | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 6.17 | 18 | 16.2857 | 7 (installed 2016) | 99.99 | [5 empty] | UUG0795
United Utilities | MIDDLETON OVERTON WWTW MIDDL | MIDDLETON/OVERTON WwTW | 017270051 | 17270051 | ST | Storm tank at WwTW | SD4304057960 | 343 |  | LADES POOL ESTUARINE WATERS | N/A | Morecambe South Morecambe North | Not Applicable | Commissioned in 2016 - full year data expected | 61.09 | 6 | 9.4286 | 7 (installed 2016) | 99.95 | [5 empty] | UUG0796
United Utilities | HAVERIGG PUMPING STATION | Haverigg PS | 017480403 | BRW0005 | SO | Storm discharge at pumping station | SD1608078760 | GB641211172000 | Duddon Sands | HAVERIGG POOL | 134 Duddon | Haverigg; Walney Biggar Bank; Walney West Shore; Walney Sandy Gap | Not Applicable | Commissioned in 2017 - full year data expected | 582.15 | 63 | 31.3333 | 6 (installed 2017) | 99.99 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0797
United Utilities | BAZIL LANE PUMPING STATION | Bazil Lane PS | NPSWQD010716 | LAN0034 | SO | Storm discharge at pumping station | SD4411057280 | 343 |  | CHAPEL POOLTRIB LUNE ESTUARY | N/A | Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 24.48 | 41 | 24.3333 | 6 (installed 2017) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0798
United Utilities | WARDLE BRIDGE PUMPING STATION | Wardle Bridge PS | 016892468 | CON0006 | SO | Storm discharge at pumping station | SJ7067066120 | GB112068055460 | Croco | THE RIVER CROCO | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 121.69 | 46 | 50.8333 | 6 (installed 2017) | 99.99 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0799
United Utilities | NANTWICH ROAD CHESTER RD CSO 131J6 | Nantwich Road/Chester Road CSO | 01CON0009 | CON0009 | SO | SO on sewer network | SJ6947066690 | GB112068055380 | Wheelock (Fowle Brook to Dane) | RIVER WHEELOCK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.73 | 4 | 49 | 5 (installed 2018) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0800
United Utilities | NANTWICH ROAD CHESTER RD CSO 131J6 | Chester Road (Middlewich) WwNPS | 01CON0010 | CON0010 | SO | Storm discharge at pumping station | SJ6947066690 | GB112068055380 | Wheelock (Fowle Brook to Dane) | Wheelock (Fowle Brook to Dane) | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 187.73 | 64 | 49.3333 | 3 (installed 2020) | 99.64 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0801
United Utilities | 5 CROXTON RD PS | Croxton Road (Middlewich No. 5 PS) | 01CON0011 | CON0011 | SO | Storm discharge at pumping station | SJ6948066950 | GB112068055380 | Wheelock (Fowle Brook to Dane) | RIVER WHEELOCK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 9.34 | 11 | 10.75 | 4 (installed 2019) | 97.7 | [5 empty] | UUG0802
United Utilities | GASWORKS YARD PUMPING STATION | Gas Yard Pumping Station | 01CON0012 | CON0012 | SO | Storm discharge at pumping station | SJ7035066410 | GB112068055460 | Croco | RIVER CROCO | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 64.08 | 32 | 41 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0803
United Utilities | GASWORKS YARD PUMPING STATION | Gas Yard Pumping Station | 01CON0012 | CON0012 | SO | Storm discharge at pumping station | SJ7035066410 | GB112068055460 | Croco | RIVER CROCO | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 7.88 | 7 | 37 | 7 (installed 2016) | 100 |  |  |  |  | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0804
United Utilities | ST MICHAELS WAY CSO | St. Michael's Way Combined Sewer Overflow (Site ID 132TH) (CON0039) | 01CON0039 | CON0039 | SO | SO on sewer network | SJ6946066700 | GB112068055380 | Wheelock (Fowle Brook to Dane) | RIVER WHEELOCK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 14.53 | 34 | 42 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0805
United Utilities | OVERTON GARDEN TERRACE PS | Garden Terrace Pumping Station (Site ID GARDE) (LAN0098) | 01LAN0098 | LAN0098 | SO | Storm discharge at pumping station | SD4234058510 | 343 |  | TRIB RIVER LUNE | N/A | Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 169.23 | 8 | 1.6667 | 6 (installed 2017) | 100 | [5 empty] | UUG0806
United Utilities | MILLOM WASTEWATER TREATMENT WORKS | MILLOM WwTW | 017470048 | 17470048 | ST | Storm tank at WwTW | SD1922079410 | 344 |  | DUDDON ESTUARY | N/A | N/A | UV (Ultraviolet) | Commissioned in 2017 - full year data expected | 1373.62 | 96 | 19 | 6 (installed 2017) | 99.93 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0807
United Utilities | KING STREET PUMPING STATION | King Street PS | 017470009 | COP0049 | SO | Storm discharge at pumping station | SD1783180401 | 187 |  | DUDDON ESTUARY | N/A | Haverigg; Walney Biggar Bank; Walney West Shore; Walney Sandy Gap | Not Applicable | Commissioned in 2017 - full year data expected | 12.43 | 19 | 16 | 6 (installed 2017) | 100 | [5 empty] | UUG0808
United Utilities | MIDDLE POOL PS MIDDP LAN0099 | Middle Pool Pumping Station (Site ID MIDDP) (LAN0099) | 017280289 | LAN0099 | SO | Storm discharge at pumping station | SD4348058330 | GB112072065950 | Overton Dyke | LADES POOL | N/A | Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 1.75 | 2 | 1.6667 | 6 (installed 2017) | 97.77 | [5 empty] | UUG0809
United Utilities | OVERTON PEDDAR-FAR PS | Overton Peddar Far PS | 017280291 | LAN0101 | SO | Storm discharge at pumping station | SD4328057900 | GB112072065950 | Overton Dyke | LADES POOL, TRIB RIVER LUNE | N/A | Morecambe South | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0810
United Utilities | MERE BROW WWTW | MERE BROW WwTW | 017030002 | 17030002 | SO | Inlet SO at WwTW | SD4240018870 | GB112070064880 | Back Drain and Sluice | TARLETON RUNNER | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 130.88 | 25 | 28.1429 | 7 (installed 2016) | 99.92 | [5 empty] | UUG0811
United Utilities | MERE BROW WWTW | MERE BROW WwTW | 017030002 | 17030002 | ST | Storm tank at WwTW | SD4240018870 | GB112070064880 | Back Drain and Sluice | TARLETON RUNNER | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 1018.66 | 127 | 160.1429 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0812
United Utilities | ARNSIDE PROMENADE PUMPING STATION | Arnside Promenade Pumping Station (Site ID 39042) (LAK0002) | 017370203 | LAK0002 | SO | Storm discharge at pumping station | SD4573078950 | 183 |  | R. KENT ESTUARY, MORECAMBE BAY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 24.76 | 33 | 25.6667 | 6 (installed 2017) | 100 | [5 empty] | UUG0813
United Utilities | NORTH WIRRAL WWTW | North Wirral WwTW (Meols) | 016993400 | 16993400 | SO | Inlet SO at WwTW | SJ2415090250 | GB112068060530 | The Birket including Arrowe Brook and Fender | River Birket | N/A | 0 | Not Applicable | Commissioned in 2016 - full year data expected | 1325.75 | 160 | 30.5714 | 7 (installed 2016) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0814
United Utilities | NORTH WIRRAL WWTW | North Wirral WwTW (Meols) | 016993400 | 16993400 | SO | Inlet SO at WwTW | SJ2150095300 | GB112068060530 | The Birket including Arrowe Brook and Fender | Liverpool Bay | N/A | Meols | Not Applicable | Commissioned in 2016 - full year data expected | 98.92 | 15 | 87.7143 | 7 (installed 2016) | 100 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Resolved - Dec | Other investigation - non-WINEP/Green Recovery | UUG0815
United Utilities | BLACK HORSE HILL CSO 511EV | Black Horse Hill CSO | 016892458 | WIR0017 | SO | SO on sewer network | SJ2294087780 | GB112068060530 | The Birket including Arrowe Brook and Fender | NEWTON BROOK TRIB OF R.BIRKET | N/A | West Kirby | Not Applicable | Commissioned in 2017 - full year data expected | 0 | 0 | 0.16667 | 6 (installed 2017) | 100 | [5 empty] | UUG0816
United Utilities | WASTDALE DRIVE CSO | Wastdale Drive CSO | 016892255 | WIR0074 | SO | SO on sewer network | SJ2492090200 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | N/A | Moreton | Not Applicable | Commissioned in 2016 - full year data expected | 210.26 | 56 | 49 | 7 (installed 2016) | 99.03 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0817
United Utilities | GARRICK AVENUE CSO | Garrick Avenue CSO | 016892439 | WIR0075 | SO | SO on sewer network | SJ2526089670 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | N/A | Moreton | Not Applicable | Commissioned in 2016 - full year data expected | 2.37 | 3 | 13.2857 | 7 (installed 2016) | 99.99 | [5 empty] | UUG0818
United Utilities | 389 HOYLAKE ROAD CSO | 389 Hoylake Road CSO | 016892440 | WIR0077 | SO | SO on sewer network | SJ2549089490 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | N/A | Moreton | Not Applicable | Commissioned in 2016 - full year data expected | 13.3 | 4 | 16.1429 | 7 (installed 2016) | 97.67 | [5 empty] | UUG0819
United Utilities | SAUGHALL MASSIE RD/DEVONSHIRE RDCSO | Saughall Massie Road / Devonshire Road CSO | 01WIR0078 | WIR0078 | SO | SO on sewer network | SJ2540088540 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | N/A | Moreton | Not Applicable | Commissioned in 2016 - full year data expected | 41.23 | 29 | 19.2857 | 7 (installed 2016) | 100 | [5 empty] | UUG0820
United Utilities | ACTON LANE COMBINED SEWER OVERFLOW | Acton Lane CSO | 016892441 | WIR0079 | SO | SO on sewer network | SJ2552089270 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | N/A | Moreton | Not Applicable | Commissioned in 2016 - full year data expected | 2.27 | 4 | 2.8571 | 7 (installed 2016) | 100 | [5 empty] | UUG0821
United Utilities | KINGFISHER WAY CSO | Kingfisher Way CSO | 016892442 | WIR0080 | SO | SO on sewer network | SJ2554088920 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | N/A | Meols | Not Applicable | Commissioned in 2016 - full year data expected | 0.47 | 2 | 5.1429 | 7 (installed 2016) | 99.97 | [5 empty] | UUG0822
United Utilities | 97 WOOD LANE CSO | 97 Wood Lane CSO | 016892443 | WIR0081 | SO | SO on sewer network | SJ2556088180 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | N/A | N/A | Not Applicable | Dec 2023 | 3469.33 | 201 |  | <1 yr (installed 2023) | 59.5745 | Installation set-up/design issue | N/A - Ongoing investigation | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0823
United Utilities | WOOD LANE/GLENTREE CLOSE CSO | Wood Lane/ Glentree Close CSO | 016892444 | WIR0083 | SO | SO on sewer network | SJ2556188181 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK TRIB R. BIRKETT | N/A | N/A | Not Applicable | Dec 2023 | 165.37 | 36 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0824
United Utilities | OUTSIDE 81 WODLANE CSO 513OI | Outside 81 Wood Lane CSO | 01WIR0084 | WIR0084 | SO | SO on sewer network | SJ2580088260 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 22.2 | 18 | 24.1667 | 6 (installed 2017) | 100 | [5 empty] | UUG0825
United Utilities | GREASBY ROAD/CORTSWAY CSO 511WQ | Greasby Road/ Cortsway Combined Sewer Overflow (Site ID 511WQ) (WIR0085) | 01WIR0085 | WIR0085 | SO | SO on sewer network | SJ2634088090 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 15.33 | 8 | 7.6667 | 6 (installed 2017) | 99.45 | [5 empty] | UUG0826
United Utilities | ARROWEBROOK LANE CSO | Arrowe Road / Arrowe Brook Lane CSO | 016892464 | WIR0086 | SO | SO on sewer network | SJ2645086930 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK TRIB RIVER BIRKET | N/A | Wallasey | Not Applicable | Commissioned in 2016 - full year data expected | 133.84 | 65 | 90.2857 | 7 (installed 2016) | 68.86 | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0827
United Utilities | FRANKBY CLOSE CSO 513MM | Frankby Close CSO | 01WIR0087 | WIR0087 | SO | SO on sewer network | SJ2481087060 | GB112068060530 | The Birket including Arrowe Brook and Fender | GREASBY BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 36.93 | 24 | 29.5 | 6 (installed 2017) | 100 | [5 empty] | UUG0828
United Utilities | WHITEBEAM WALK CSO 513PX | Whitebeam Walk CSO | 016892263 | WIR0088 | SO | SO on sewer network | SJ2484086900 | GB112068060530 | The Birket including Arrowe Brook and Fender | GREASBY BROOK TRIB ARROW BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 32.4 | 25 | 27.8333 | 6 (installed 2017) | 100 | [5 empty] | UUG0829
United Utilities | STANLEY ROAD PUMPING STATION | Stanley Road Pumping Station (Site ID 51005) (WIR0090) | 016892431 | WIR0090 | SO | Storm discharge at pumping station | SJ2036088320 | GB112068060530 | Mersey Estuary | THE IRISH SEA | N/A | West Kirby; Meols | Not Applicable | Commissioned in 2016 - full year data expected | 0.19 | 1 | 2.4286 | 7 (installed 2016) | 100 | [5 empty] | UUG0830
United Utilities | Harrington Avenue CSO | Harrington Avenue CSO | 16892362 | WIR0091 | SO | SO on sewer network | SJ2236088970 | GB112068060530 | The Birket including Arrowe Brook and Fender | TRIB CARR DRAIN (TO R. BIRKET) | N/A | Wallasey | Not Applicable | Commissioned in 2016 - full year data expected | 117.5 | 46 | 40.1429 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0831
United Utilities | GREENBANK ROAD/ROSSALL ROAD CSO | Greenbank Road pumping station (Site ID 51001) (WIR0092) | EPRQB3593VE | WIR0092 | SO | Storm discharge at pumping station | SJ2178087720 | GB112069064720 | The Birket including Arrowe Brook and Fender | Un-named tributary of the River Birket | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 0.09 | 1 | 2 | 7 (installed 2016) | 99.24 | [5 empty] | UUG0832
United Utilities | SANDSIDE PUMPING STATION | Sandside PS | 017370202 | LAK0057 | SO | Storm discharge at pumping station | SD4779080770 | 182 |  | RIVER BELA | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 4.09 | 2 | 1.5 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0833
United Utilities | LONG HEY ROAD CSO | Long Hey Road CSO | CM0077001 | WIR0094 | SO | SO on sewer network | SJ2302083940 | GB641211630001 | Mersey Mouth | RIVER DEE (NORTH WALES) | 18 Dee | West Kirby | Not Applicable | Commissioned in 2016 - full year data expected | 27.73 | 12 | 16.8571 | 7 (installed 2016) | 99.99 | [5 empty] | UUG0834
United Utilities | REAR OF 65 FULTON AVE CSO 5130R | Rear of 65 Fulton Avenue CSO | 016881738 | WIR0136 | SO | SO on sewer network | SJ2313087300 | GB112068060530 | The Birket including Arrowe Brook and Fender | NEWTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 74.03 | 32 | 23.5 | 6 (installed 2017) | 96.15 | [5 empty] | UUG0835
United Utilities | ENNISDALE DRIVE CSO | Ennisdale Drive CSO | 016982966 | WIR0142 | SO | SO on sewer network | SJ2293087780 | GB112068060530 | The Birket including Arrowe Brook and Fender | NEWTON BROOK | N/A | West Kirby | Not Applicable | Commissioned in 2016 - full year data expected | 0.43 | 3 | 3.8571 | 7 (installed 2016) | 97.81 | [5 empty] | UUG0836
United Utilities | MELMERBY STW | MELMERBY WwTW | 017670068 | 17670068 | SO | Inlet SO at WwTW | NY6010037660 | GB102076073810 | Robberby Water | MELMERBY (DALE) BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 12.3 | 10 | 16 | 4 (installed 2019) | 99.95 | [5 empty] | UUG0837
United Utilities | UNTHANK PUMPING STATION | Unthank PS | 017680386 | EDE0111 | SO | Storm discharge at pumping station | NY6092040390 | GB102076073820 | Glassonby Beck | HAZELRIGG BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 69.5 | 20 | 21 | 4 (installed 2019) | 100 | [5 empty] | UUG0838
United Utilities | GAMBLESBY PUMPING STATION | Gamblesby PS | 017680387 | EDE0112 | SO | Storm discharge at pumping station | NY6052039500 | GB102076073820 | Glassonby Beck | GAMBLESBY BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 129.62 | 36 | 37.25 | 4 (installed 2019) | 99.98 | [5 empty] | UUG0839
United Utilities | MELLING WWTW | MELLING WwTW | 016987034 | 16987034 | SO | Inlet SO at WwTW | SJ3895098900 | GB112069061441 | Alt US Bull Bridge | UNNAMED TRIB OF RIVER ALT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 36.5 | 8 | 1.6 | 5 (installed 2018) | 99.92 | [5 empty] | UUG0840
United Utilities | MARTON NORTH WWTW | MARTON NORTH (Cassia) WwTW | 016810093 | 16810093 | SO | Inlet SO at WwTW | SJ6205067880 | GB112068060540 | Bogart Brook | BOGART BROOK | N/A | N/A | Not Applicable | Dec 2023 | 0 | 0 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0841
United Utilities | MADLEY WWTW | MADELEY WwTW | 016810091 | 16810091 | ST | Storm tank at WwTW | SJ7700045090 | GB112068055200 | Lea | RIVER LEA | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 159.92 | 18 | 30.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG0842
United Utilities | OFF MOSS LANE MADELEY CSO | Moss Lane (Madley) Combined Sewer Overflow | 01NEW0005 | NEW0005 | SO | SO on sewer network | SJ7722044970 | GB112068055200 | Lea | RIVER LEA | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 146.17 | 42 | 84.5 | 4 (installed 2019) | 97.31 |  |  | Data collection - EDM non-representative location | Resolved - May | Other investigation - non-WINEP/Green Recovery | UUG0843
United Utilities | NEWCASTLE ROAD CSO | NEWCASTLE ROAD CSO | 01NEW0006 | NEW0006 | SO | SO on sewer network | SJ7816045520 | GB112068055230 | Checkley Brook - Upper | HAZELEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 126.03 | 46 | 73.2 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0844
United Utilities | FIELD NO.4649 OFF KEELE ROAD CSO | Field No. 4649 (off Keele Road) CSO | 01NEW0007 | NEW0007 | SO | SO on sewer network | SJ7838045470 | GB112068055230 | Checkley Brook - Upper | HAZELEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 3.75 | 4 (installed 2019) | 100 | [5 empty] | UUG0845
United Utilities | STATION ROAD CSO | STATION ROAD (Keele) CSO | 01NEW0008 | NEW0008 | SO | SO on sewer network | SJ7963045770 | GB112071065490 | Checkley Brook via Hazeley Brook | RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 30.53 | 32 | 39 | 3 (installed 2020) | 100 | [5 empty] | UUG0846
United Utilities | MACCLESFIELD WWTW | MACCLESFIELD WwTW | 016910009 | 16910009 | ST | Storm tank at WwTW | SJ8961078200 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 827.05 | 128 | 99.5 | 4 (installed 2019) | 100 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0847
United Utilities | ROEWOODS OUTFALL SEWER | Roewoods Outfall Sewer (27206) (MAC0028) | 01MAC0028 | MAC0028 | SO | SO on sewer network | SJ9030075060 | GB112069061320 | Bollin (Source to Dean) | UN-NAMED TRIB OF RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 56.1 | 43 | 40.2 | 5 (installed 2018) | 97.02 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0848
United Utilities | 20 ADLINGTON ROAD CSO | 20 Adlington Road CSO | 016892094 | MAC0053 | SO | SO on sewer network | SJ9306078000 | GB112069061360 | Dean (Bollington to Bollin) | RIVER DEAN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 370.67 | 90 | 97 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0849
United Utilities | ALLEN ST/LORD ST CSO | Allen Street/Lord Street CSO | EPRSB3793EM | MAC0054 | SO | SO on sewer network | SJ9374077640 | GB112069060650 | Dean (Lamaload to Bollington) | RIVER DEAN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.4 | 4 | 4 | 3 (installed 2020) | 99.99 | [5 empty] | UUG0850
United Utilities | WATER STREET CSO | Water Street CSO | EPRSB3793VY | MAC0056 | SO | SO on sewer network | SJ9351677848 | GB112069061360 | Dean (Bollington to Bollin) | RIVER DEAN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 15.5 | 24 | 28 | 5 (installed 2018) | 100 | [5 empty] | UUG0851
United Utilities | RIVER BANK CSO | River Bank Close CSO | EPRSB3793RW | MAC0055 | SO | SO on sewer network | SJ9274077660 | GB112069061360 | Dean (Bollington to Bollin) | RIVER DEAN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 178.9 | 94 | 93 | 5 (installed 2018) | 98.54 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0852
United Utilities | WESTMINSTER ROAD CSO | Westminster Road CSO | 016892096 | MAC0062 | SO | SO on sewer network | SJ9118074470 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 140.49 | 82 | 104 | 5 (installed 2018) | 79.16 | Sensor failure / issue | Resolved - Jul | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP or Green Recovery | UUG0853
United Utilities | CARTMEL CLOSE CSO | Cartmel Close (Macclesfield) Combined Sewer Overflow (Site ID 273BV) (MAC0061) | 016892095 | MAC0061 | SO | SO on sewer network | SJ9082075120 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 43.27 | 14 | 42 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0854
United Utilities | BANBURY CLOSE CSO | Banbury Close CSO | 01MAC0064 | MAC0064 | SO | SO on sewer network | SJ9227074880 | GB112069061320 | Bollin (Source to Dean) | SHORESCLOUGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 7.4 | 22 | 22 | 4 (installed 2019) | 100 | [5 empty] | UUG0855
United Utilities | WATERS GREEN (DAMS VALLEY) CSO | Waters Green (Dams Valley) CSO | 01MAC0065 | MAC0065 | SO | SO on sewer network | SJ9195073552 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2.03 | 11 | 13.8 | 5 (installed 2018) | 99.47 | [5 empty] | UUG0856
United Utilities | CSO AT 18/20 BEECH FARM DRIVE | 18/20 Beech Farm Drive CSO | 016892097 | MAC0063 | SO | SO on sewer network | SJ9154074560 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0857
United Utilities | ADLINGTON ROAD CSO (271A4) | Adlington Road (Bollington Park) CSO | 01MAC0120 | MAC0120 | SO | SO on sewer network | SJ9310078010 | GB112069061360 | Dean (Bollington to Bollin) | RIVER DEAN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 39.97 | 37 | 37 | 4 (installed 2019) | 100 | [5 empty] | UUG0858
United Utilities | PALMERSTON ST SHRIGLEY RD 272KZ | Palmerston Street/Shrigley Road CSO | 01MAC0121 | MAC0121 | SO | SO on sewer network | SJ9395077990 | GB112069060660 | Harrop Brook | HARROP BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 20.47 | 28 | 152.25 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0859
United Utilities | HIBEL ROAD CSO 27075 | Hibel Road CSO | 016982179 | MAC0146 | SO | SO on sewer network | SJ9177074450 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 56.04 | 30 | 24.2 | 5 (installed 2018) | 94.76 | [5 empty] | UUG0860
United Utilities | BEECH BRIDGE SOUTH CSO | BEECH BRIDGE SOUTH CSO | 01MAC0126 | MAC0126 | SO | SO on sewer network | SJ9149074550 | GB112069061320 | Bollin (Source to Dean) | RIVER BOLLIN | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0861
United Utilities | LOW MARPLE STW | LOW MARPLE WwTW | 016940178 | 16940178 | ST | Storm tank at WwTW | SJ9608090500 | GB112069061050 | Etherow (Glossop Brook to Goyt) | RIVER ETHEROW | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 745.25 | 85 | 78 | 4 (installed 2019) | 98.58 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0862
United Utilities | COMPSTALL RD (NEAR IRONBRIDGE) CSO | Compstall Road CSO | 01STK0052 | STK0052 | SO | SO on sewer network | SJ9643090200 | GB112069060960 | Goyt (Sett to Etherow) | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 159.53 | 31 | 18.8571 | 7 (installed 2016) | 100 | [5 empty] | UUG0863
United Utilities | TOWN STREET COMBINED SEWER OVERFLOW | Town Street Combined Sewer Overflow (Site ID 439AB) (STK0138) | 016982519 | STK0138 | SO | SO on sewer network | SJ9649089440 | GB112069060960 | Goyt (Sett to Etherow) | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 209.86 | 34 | 34.1429 | 7 (installed 2016) | 100 | [5 empty] | UUG0864
United Utilities | COMPSTALL ROAD CSO | Compstall Road CSO | 016982502 | STK0139 | SO | SO on sewer network | SJ9643090690 | GB112069061050 | Etherow (Glossop Brook to Goyt) | RIVER ETHEROW | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 12.5 | 4 (installed 2019) | 100 | [5 empty] | UUG0865
United Utilities | LOW HESKET STW | LOW HESKET WwTW | 017670104 | 17670104 | SO | Inlet SO at WwTW | NY4603045550 | GB102076074030 | Petteril d/s Blackrack Beck | RIVER PETTERIL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 122.59 | 44 | 44.5 | 4 (installed 2019) | 100 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0866
United Utilities | LOW HESKET PS | Low Hesket PS | 017680337 | EDE0088 | SO | Storm discharge at pumping station | NY4636046470 | GB102076074030 | Petteril d/s Blackrack Beck | BARROCK GILL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 111.1 | 33 | 32 | 4 (installed 2019) | 26.37 | Sensor failure / issue | N/A - Ongoing investigation |  |  |  | UUG0867
United Utilities | LOW BENTHAM WWTW (LOWBE) | LOW BENTHAM WwTW | 017260007 | 17260007 | ST | Storm tank at WwTW | SD6357069620 | GB112072065990 | Wenning - Lower | RIVER WENNING | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 53.5 | 4 (installed 2019) | 90.38 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0868
United Utilities | LORTON STW | LORTON WwTW | 017570046 | 17570046 | SO | Inlet SO at WwTW | NY1497026450 | GB112075070400 | Cocker - conf Whit Beck to conf Derwent | RIVER COCKER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 36.13 | 51 | 41.3333 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0869
United Utilities | LONGTOWN WWTW | LONGTOWN WwTW | 017770003 | 17770003 | ST | Storm tank at WwTW | NY3751068430 | GB102077074190 | Esk (Eden and Esk) | RIVER ESK (BORDER) | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 260.86 | 52 | 58 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0870
United Utilities | LONGTOWN WWTW | LONGTOWN WwTW | 017770003 | 17770003 | SO | Inlet SO at WwTW | NY3751068430 | GB102077074190 | Esk (Eden and Esk) | RIVER ESK (BORDER) | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 55 | 34 | 43.75 | 4 (installed 2019) | 100 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0871
United Utilities | LONGTON WASTEWATER TREATMENT WORKS | LONGTON WwTW | 017060019 | 17060019 | ST | Storm tank at WwTW | SD4687025280 | GB112070064900 | Tarra Carr Gutter | TARRA CARR GUTTER | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 2063.83 | 146 | 64.8571 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0872
United Utilities | JUNC PROMENADE SILVERDALE RD CSO | Arnside Promenade/Silverdale Road CSO | EPRYP3621XD | LAK0101 | SO | SO on sewer network | SD4558678760 | 183 |  | MORECAMBE BAY ESTUARINE WTRS | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 147.5 | 42 | 7 | 6 (installed 2017) | 99.99 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0873
United Utilities | LONDON ROAD NANTWICH CSO | London Road (Nantwich) Combined Sewer Overflow (Site ID 162C7) (CRE0081) | 016881771 | CRE0081 | SO | SO on sewer network | SJ6507053130 | 176 |  | RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0 | 4 (installed 2019) | 100 | [5 empty] | UUG0874
United Utilities | LONG PRESTON WWTW LNGPR | Long Preston Wastewater Treatment Works (LNGPR) (017160041) | 017160041 | 17160041 | SO | Inlet SO at WwTW | SD8306057620 | GB112071065600 | Long Preston Beck | LONG PRESTON BECK TRIB R RIBBL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1421.13 | 115 | 137.4 | 5 (installed 2018) | 99.99 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0875
United Utilities | WOOLTON STW | Woolton WwTW | 016930122 | 16930122 | SO | Inlet SO at WwTW | SJ4495087460 | GB112069061390 | Ditton Brook (Halewood to Mersey Estuary) | HALEWOOD BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 26.77 | 28 | 25 | 3 (installed 2020) | 99.66 | [5 empty] | UUG0876
United Utilities | WOOLTON STW | Woolton WwTW | 016930122 | 16930122 | ST | Storm tank at WwTW | SJ4495087460 | GB112069061390 | Ditton Brook (Halewood to Mersey Estuary) | HALEWOOD BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 229.35 | 41 | 31.3333 | 3 (installed 2020) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0877
United Utilities | NETHER KELLET WTW NETHK | NETHER KELLET WwTW | 017370074 | 17370074 | ST | Storm tank at WwTW | SD5018068160 | 185 |  | NETHER BECK, TRIB RIVER KEER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1227.69 | 83 | 83.8 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0878
United Utilities | LOWER RD PS | Lower Road PS | 01KNW0007 | KNW0007 | SO | Storm discharge at pumping station | SJ4592085900 | GB112069061390 | Ditton Brook (Halewood to Mersey Estuary) | TRIB DITTON BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0879
United Utilities | NEWTON ARLOSH WEST PUMPING STATION | Newton Arlosh West PS | 017580259 | ALL0108 | SO | Storm discharge at pumping station | NY1942054480 | 90 |  | TRIBUTARY OF RIVER WAMPOOL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2328.21 | 123 | 53.8 | 5 (installed 2018) | 70.62 | Sensor failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0880
United Utilities | REAR OF SUNNYSIDE TERRACE CSO | Rear of Sunnyside Terrace CSO | 017280303 | WYR0067 | SO | SO on sewer network | SD3717047380 | 180 |  | TRIBUTARY OF COCKERS DYKE | N/A | Fleetwood | Not Applicable | Commissioned in 2016 - full year data expected | 0 | 0 | 17.5714 | 7 (installed 2016) | 100 | [5 empty] | UUG0881
United Utilities | PRESTON WASTEWATER TREATMENT WORKS | PRESTON WwTW | 017160064 | 17160064 | ST | Storm tank at WwTW | SD4571027930 | 176 |  | RIVER RIBBLE ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 1177.56 | 86 | 74 | 6 (installed 2017) | 36.75 | Sensor failure / issue | N/A - Ongoing investigation | Data collection - EDM non-representative location | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0882
United Utilities | LAMALEACH CSO 19008 | Lamaleach CSO | 01FYL0002 | FYL0002 | SO | SO on sewer network | SD4250028200 | 176 |  | POOL STREAM | N/A | Southport; St Annes Pier; St. Annes North; Blackpool South | Not Applicable | Commissioned in 2018 - full year data expected | 206.86 | 29 | 31.4 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0883
United Utilities | LYTHAM PUMPING STATION | Lytham PS | 017160106 | FYL0003 | SO | Storm discharge at pumping station | SD3835027650 | 176 |  | LIGGARD BROOK | N/A | Southport; St Annes Pier; St. Annes North; Blackpool South | Not Applicable | Commissioned in 2016 - full year data expected | 116.26 | 45 | 50 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0884
United Utilities | SANDGATE PUMPING STATION NO 2 | SANDGATE PUMPING STATION | 01FYL0005 | FYL0005 | SO | Storm discharge at pumping station | SD3130029500 | 350 |  | THE IRISH SEA | N/A | Morecambe North | Not Applicable | Commissioned in 2019 - full year data expected | 0.81 | 1 | 2.75 | 4 (installed 2019) | 99.99 | [5 empty] | UUG0885
United Utilities | GOWER ST/KINGS DOCK CSO | Gower Street/Kings Dock CSO | 016930975 | LIV0030 | SO | SO on sewer network | SJ3400089700 | GB112070064820 | MERSEY | MERSEY ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2.99 | 4 | 11 | 5 (installed 2018) | 99.72 | [5 empty] | UUG0886
United Utilities | BROOK CORNER CSO | Brook Corner CSO | 01FYL0015 | FYL0015 | SO | SO on sewer network | SD3970027701 | 176 |  | RIVER RIBBLE | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 77.4 | 12 | 8.7143 | 7 (installed 2016) | 99.28 | [5 empty] | UUG0887
United Utilities | NAZE LANE PUMPING STATION | Naze Lane PS (19048) | 017180397 | FYL0018 | SO | Storm discharge at pumping station | SD4233027040 | 176 |  | POOL STREAM | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1554.37 | 127 | 110.2 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0888
United Utilities | FAIRHAVEN PS | Fairhaven PS (Discharge to Estuary) | 17180556 | FYL0042 | SO | Storm discharge at pumping station | SD3376026030 | 176 |  | RIVER RIBBLE | 111 Ribble | St Annes Pier; St. Annes North; Blackpool South | Not Applicable | Commissioned in 2018 - full year data expected | 64.41 | 14 | 19.8 | 5 (installed 2018) | 100 | [5 empty] | UUG0889
United Utilities | FAIRHAVEN PS | Fairhaven PS (Discharge to Estuary) | 17180556 | FYL0042 | SO | Storm discharge at pumping station | SD3376026030 | 176 |  | RIVER RIBBLE | 111 Ribble | St Annes Pier; St. Annes North; Blackpool South | Not Applicable | Commissioned in 2018 - full year data expected | 6.19 | 5 | 6.8 | 5 (installed 2018) | 96.43 | [5 empty] | UUG0890
United Utilities | ALBYN STREET EAST CSO 33102 | Albyn Street East CSO | 017160851 | PRE0002 | SO | SO on sewer network | SD5493029330 | 176 |  | SWILLBROOK CLVRT TRIB R RIBBLE | N/A | Southport; St Annes Pier; St. Annes North; Blackpool South | Not Applicable | Commissioned in 2018 - full year data expected | 100.5 | 18 | 16.2 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0891
United Utilities | RIBBLETON LANE CSO 33103 | Ribbleton Lane CSO | 017160312 | PRE0004 | SO | SO on sewer network | SD5528028740 | 176 |  | RIVER RIBBLE TIDAL VIA SWS | N/A | Southport; St Annes Pier; St. Annes North; Blackpool South | Not Applicable | Commissioned in 2018 - full year data expected | 122.18 | 14 | 17 | 5 (installed 2018) | 100 | [5 empty] | UUG0892
United Utilities | PERCY STREET CSO | Percy Street CSO | 017190768 | PRE0003 | SO | SO on sewer network | SD5528128742 | 176 |  | STORM CULVERT,TRIB OF RIBBLE | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0893
United Utilities | ST PAUL'S ROAD CSO | St Paul's Road combined sewer overflow (332TX) (PRE0006) | 016881649 | PRE0006 | SO | SO on sewer network | SD5196329367 | 171 |  | THE MERSEY ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2.1 | 6 | 113.2 | 5 (installed 2018) | 99.07 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0894
United Utilities | LONDON ROAD | London Road CSO | 017160314 | PRE0005 | SO | SO on sewer network | SD5528028742 | 176 |  | STORM CULVERT INTO R RIBBLE | N/A | N/A | Not Applicable | Commissioned pre-2016 - full year data expected | 0.75 | 3 | 0.4 | 8 (installed 2015) | 100 | [5 empty] | UUG0895
United Utilities | 18 DEEPDALE ROAD | 18 Deepdale Road CSO | 017190864 | PRE0020 | SO | SO on sewer network | SD5528028741 | 176 |  | RIVER RIBBLE VIA STORM CULVERT | N/A | N/A | Not Applicable | Commissioned pre-2016 - full year data expected | 0 | 0 | 0 | 8 (installed 2015) | 100 | [5 empty] | UUG0896
United Utilities | MARSH LANE CSO PRE0021 | Marsh Lane CSO | 017190874 | PRE0021 | SO | SO on sewer network | SD5269129413 | 176 |  | RIVER RIBBLE VIA CHAIN CULVERT | N/A | St Annes | Not Applicable | Commissioned pre-2016 - full year data expected | 0 | 0 | 0 | 8 (installed 2015) | 100 | [5 empty] | UUG0897
United Utilities | MOORBROOK STREET CSO 332F2 | MOORBROOK STREET CSO | PRE0023 | PRE0023 | SO | SO on sewer network | SD5354930499 | 176 |  | CLVRT MOOR BROOK TRIB RVR RIBB | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 201.3 | 23 | 14.6 | 5 (installed 2018) | 99.52 | [5 empty] | UUG0898
United Utilities | ST GEORGES ROAD CSO | St George's Road CSO | 017160320 | PRE0024 | SO | SO on sewer network | SD5482030450 | 176 |  | MOORE BROOK CULVERT | N/A | Southport; St Annes Pier; St. Annes North; Blackpool South | Not Applicable | Commissioned in 2018 - full year data expected | 8.4 | 17 | 14.2 | 5 (installed 2018) | 100 | [5 empty] | UUG0899
United Utilities | Garston CSO | Garston CSO | 16930986 | LIV0054 | SO | SO on sewer network | SJ3959083420 | GB531206908100 | MERSEY | MERSEY ESTUARY | N/A | N/A | Not Applicable | Dec 2023 | 85.04 | 53 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0900
United Utilities | FISHERGATE HILL CSO (CHAMBER C9) | Fishergate Hill CSO | 017190875 | PRE0022 | SO | SO on sewer network | SD5286928868 | 176 |  | RIVER RIBBLE | N/A | St Annes | Not Applicable | Commissioned pre-2016 - full year data expected | 639.26 | 30 | 3.8 | 8 (installed 2015) | 100 | [5 empty] | UUG0901
United Utilities | POWIS ROAD CSO 332MG PRE0025 | Powis Road CSO | 017160321 | PRE0025 | SO | SO on sewer network | SD5140229892 | 176 |  | CHAIN CAUL CULVERT | N/A | Southport; St Annes Pier; St. Annes North; Blackpool South | Not Applicable | Commissioned in 2018 - full year data expected | 10.86 | 4 | 0.8 | 5 (installed 2018) | 100 | [5 empty] | UUG0902
United Utilities | RIVERSIDE ROAD PUMPING STATION | Riverside Road pumping station (Site ID 38026) (SEF0083) | 01SEF0083 | SEF0083 | SO | Storm discharge at pumping station | SD2960003650 | GB531206908300 | ALT | RIVER ALT ESTUARINE WATERS | N/A | Formby | Not Applicable | Commissioned in 2016 - full year data expected | 9.6 | 49 | 49.2857 | 7 (installed 2016) | 99.45 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0903
United Utilities | WOLSELEY ROAD CSO | Wolseley Road CSO | 017160324 | PRE0028 | SO | SO on sewer network | SD5311028280 | 176 |  | RIVER RIBBLE | N/A | Southport; St Annes Pier; St. Annes North; Blackpool South | Not Applicable | Commissioned in 2018 - full year data expected | 101.09 | 13 | 12.4 | 5 (installed 2018) | 100 | [5 empty] | UUG0904
United Utilities | DIBBS LANE CSO 381RT | O/S XX Hall Road East CSO | 016982651 | SEF0096 | SO | SO on sewer network | SD2955001650 | GB641211630001 | Mersey Mouth | RIVER MERSEY ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 70.3 | 58 | 60.3333 | 6 (installed 2017) | 99.73 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0905
United Utilities | BLACKPOOL ROAD CSO | Blackpool Road CSO | 01PRE0029 | PRE0029 | SO | SO on sewer network | SD4928030090 | 176 |  | TRIB OF THE RIVER RIBBLE | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 167.9 | 88 | 80 | 7 (installed 2016) | 99.15 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0906
United Utilities | FISHERGATE HILL CSO CHAMBER C8 | Fishergate Hill CSO | 017190876 | PRE0027 | SO | SO on sewer network | SD5283728977 | 176 |  | RIVER RIBBLE | N/A | St Annes | Not Applicable | Commissioned pre-2016 - full year data expected | 786.82 | 36 | 4.5 | 8 (installed 2015) | 100 | [5 empty] | UUG0907
United Utilities | HALSBURY STREET CSO 331XR | Halsbury Street CSO | 01PRE0072 | PRE0072 | SO | SO on sewer network | SD5461028960 | 176 |  | SWILL BROOK CLVRT RIVER RIBBLE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 21.2 | 11 | 5.8 | 5 (installed 2018) | 100 | [5 empty] | UUG0908
United Utilities | MANCHESTER RD/SELBOURNE RD CSO | Manchester Road/Selbourne Road CSO | 01PRE0074 | PRE0074 | SO | SO on sewer network | SD5470028990 | 176 |  | RIVER RIBBLE | N/A | Southport; St Annes Pier; St. Annes North; Blackpool South | Not Applicable | Commissioned in 2018 - full year data expected | 7.2 | 10 | 8 | 5 (installed 2018) | 100 | [5 empty] | UUG0909
United Utilities | GEORGE STREET CSO 331VJ | GEORGE STREET CSO | 01PRE0077 | PRE0077 | SO | SO on sewer network | SD5488029260 | 176 |  | TRIBUTARY OF RIVER RIBBLE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 241.53 | 100 | 99 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0910
United Utilities | WEST STRAND CSO CHAMBER C10 PRE0071 | West Strand CSO | 017190872 | PRE0071 | SO | SO on sewer network | SD5259329501 | 176 |  | CHAIN CAUL CULVERT INTO RIBBLE | N/A | St Annes | Not Applicable | Commissioned pre-2016 - full year data expected | 7.99 | 3 | 0.375 | 8 (installed 2015) | 100 | [5 empty] | UUG0911
United Utilities | THORNPARK PUMPING STATION 33007 | THORNPARK PS | 01PRE0082 | PRE0082 | SO | SO on sewer network | SD4983029960 | 176 |  | UNNAMED TRIB OF RVR RIBBLE | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 58.41 | 31 | 29.5714 | 7 (installed 2016) | 99.98 | [5 empty] | UUG0912
United Utilities | BANK PARADE CSO | Bank Parade CSO | 017180386 | PRE0087 | SO | SO on sewer network | SD5421028660 | 176 |  | RIVER RIBBLE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 168.56 | 53 | 10.6 | 5 (installed 2018) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0913
United Utilities | FRENCHWOOD KNOLL CSO 331UX | Frenchwood Knoll CSO | 017180524 | PRE0104 | SO | SO on sewer network | SD5425028690 | 176 |  | SWILLBROOK CULVERT | N/A | Southport; St Annes Pier; St. Annes North; Blackpool South | Not Applicable | Commissioned in 2018 - full year data expected | 54.33 | 80 | 119.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0914
United Utilities | WATERY LANE CSO SHAFT C1 PRE0093 | Watery Lane CSO (Shaft C1) | 017180497 | PRE0093 | SO | SO on sewer network | SD5240429937 | 176 |  | MOORBROOK CULVERT -> R. RIBBLE | N/A | St Annes | Not Applicable | Commissioned pre-2016 - full year data expected | 587.82 | 26 | 3.3 | 8 (installed 2015) | 99.99 | [5 empty] | UUG0915
United Utilities | 208 DEEPDALE ROAD CSO | 208 Deepdale Road CSO | 017180537 | PRE0106 | SO | SO on sewer network | SD5453030430 | 176 |  | MOOR BROOK CULVERT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 5.17 | 17 | 11.75 | 4 (installed 2019) | 100 | [5 empty] | UUG0916
United Utilities | DIBBS LANE CSO 381RT | Dibbs Lane CSO | 016982649 | SEF0094 | SO | SO on sewer network | SD2955001650 | GB641211630001 | Mersey Mouth | RIVER MERSEY ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 9.6 | 5 (installed 2018) | 93.37 | [5 empty] | UUG0917
United Utilities | WATERY LANE CSO PRE0108 | Watery Lane CSO | 017180525 | PRE0108 | SO | SO on sewer network | SD5198129844 | 176 |  | CHAIN CAUL STORM CULVERT | N/A | N/A | Not Applicable | Commissioned pre-2016 - full year data expected | 0 | 0 | 0 | 8 (installed 2015) | 100 | [5 empty] | UUG0918
United Utilities | LITTLE SALKELD WWTW | LITTLE SALKELD WwTW | 017680290 | 17680290 | SO | Inlet SO at WwTW | NY5617036670 | GB102076073940 | Eden - Eamont to tidal | TRIB RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1725.39 | 164 | 182.5 | 4 (installed 2019) | 99.94 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0919
United Utilities | LITTLE CLIFTON STW | LITTLE CLIFTON WwTW | 017570045 | 17570045 | ST | Storm tank at WwTW | NY0567029230 | GB112075070540 | Marron | RIVER MARRON | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 888 | 77 | 77.6667 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0920
United Utilities | GLEN HOUSE CSO | GLEN HOUSE CSO | 01ALL0016 | ALL0016 | SO | SO on sewer network | NY0561028770 | GB112075070540 | Marron | UNNAMED TRIB OF RIVER MARRON | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 25.27 | 34 | 79.2 | 5 (installed 2018) | 100 |  |  | Data collection - EDM non-representative location | Resolved - Oct | Other investigation - non-WINEP/Green Recovery | UUG0921
United Utilities | LINDALE WASTEWATER TREATMENT WORKS | LINDALE WwTW | 017370073 | 17370073 | ST | Storm tank at WwTW | SD4234280672 | GB112073071440 | Winster | RIVER WINSTER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1166.74 | 84 | 80.4 | 5 (installed 2018) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0922
United Utilities | DALE STREET CSO 331R7 | Dale Street CSO | 017180527 | PRE0105 | SO | SO on sewer network | SD5528028750 | 176 |  | RIVER RIBBLE TIDAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0.4 | 5 (installed 2018) | 100 | [5 empty] | UUG0923
United Utilities | LEYLAND WASTE WATER TREATMENT WORKS | LEYLAND WwTW | 017060018 | 17060018 | ST | Storm tank at WwTW | SD5215020870 | GB112070064912 | Lostock DS Farington Weir | RIVER LOSTOCK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 924.5 | 104 | 34.6667 | 3 (installed 2020) | 98.77 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0924
United Utilities | LANCASTER LANE CSO 12045 | Lancaster Lane CSO | 017081365 | CHR0005 | SO | SO on sewer network | SD5563022350 | GB112070064820 | Lostock DS Farington Weir | BOW BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 87.64 | 63 | 82 | 5 (installed 2018) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG0925
United Utilities | TOWNGATE/FOX LANE CSO | Towngate/ Fox Lane CSO | 017081318 | SRI0016 | SO | SO on sewer network | SD5401021320 | GB112070064912 | Lostock DS Farington Weir | CRICKETFIELD BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 3.87 | 8 | 3.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0926
United Utilities | COWLING LANE LEYLAND LANE CSO 401PW | Cowling Lane/Leyland Lane CSO | 01SRI0017 | SRI0017 | SO | SO on sewer network | SD5250022090 | GB112070064912 | Lostock DS Farington Weir | RIVER LOSTOCK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 409.57 | 103 | 89.1667 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0927
United Utilities | LEADALE ROAD CSO 402CQ | Leadale Road CSO | 01SRI0018 | SRI0018 | SO | SO on sewer network | SD5285022270 | GB112070064912 | Lostock DS Farington Weir | BANNISTER BROOK | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 13 | 11 | 12.7143 | 7 (installed 2016) | 100 | [5 empty] | UUG0928
United Utilities | SCHOOL LANE CSO | SCHOOL LANE CSO | 01SRI0019 | SRI0019 | SO | SO on sewer network | SD5401022460 | GB112070064912 | Lostock DS Farington Weir | BANNISTER BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 380.93 | 130 | 142.8 | 5 (installed 2018) | 99.73 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0929
United Utilities | TURPIN GREEN LANE CSO | Turpin Green Lane CSO | 017081364 | SRI0020 | SO | SO on sewer network | SD5456022510 | GB112070064912 | Lostock DS Farington Weir | BANNISTER BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 20.3 | 35 | 42.8 | 5 (installed 2018) | 95.64 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0930
United Utilities | GOLDEN HILL LANE CSO | GOLDEN HILL LANE CSO | 01SRI0022 | SRI0022 | SO | SO on sewer network | SD5292022820 | GB112070064912 | Lostock DS Farington Weir | RIVER LOSTOCK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 74.93 | 38 | 33.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0931
United Utilities | REAR 24 BISPHAM AVENUE CSO | Rear of No. 24 Bispham Avenue CSO | EPRSB3398AS | SRI0024 | SO | SO on sewer network | SD5343023820 | GB112070064911 | Lostock US Farington Weir | RIVER LOSTOCK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 100 | [5 empty] | UUG0932
United Utilities | FOWLER LANE/CROSTON ROAD CSO | FOWLER LANE / CROSTON ROAD CSO | 01SRI0025 | SRI0025 | SO | SO on sewer network | SD5398024860 | GB112070064911 | Lostock US Farington Weir | RIVER LOSTOCK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 60.23 | 20 | 18.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0933
United Utilities | 74 SLATER LANE (LEYLAND) CSO | 74 Slater Lane (Leyland) CSO | 01SRI0032 | SRI0032 | SO | SO on sewer network | SD5233021570 | GB112070064912 | Lostock DS Farington Weir | RIVER LOSTOCK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 143.2 | 50 | 57.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0934
United Utilities | O/S 50 BISPHAM AVE | Outside No. 50 Bispham Avenue | 017081264 | SRI0056 | SO | SO on sewer network | SD5335023700 | GB112070064911 | Lostock US Farington Weir | RIVER LOSTOCK | N/A | N/A | Not Applicable | Dec 2023 | 0.07 | 1 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0935
United Utilities | LEYLAND LANE (SEVEN STARS) CSO | Leyland Lane (Seven Stars) CSO | 017081265 | SRI0057 | SO | SO on sewer network | SD5276021700 | GB112070064912 | Lostock DS Farington Weir | BANNISTER BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 31 | 18 | 19.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0936
United Utilities | INGLEBROUGH WAY BOW LANE CSO 40040 | Ingleborough Way/Bow Lane CSO | 017081363 | SRI0066 | SO | SO on sewer network | SD5494022520 | GB112070064912 | Lostock DS Farington Weir | BANNISTER BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 170.29 | 79 | 86.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0937
United Utilities | LEIGH STW | LEIGH WwTW | 016920134 | 16920134 | ST | Storm tank at WwTW | SJ6581099000 | GB112069060760 | Pennington Brook (Glaze) | PENNINGTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1026.23 | 94 | 81.3333 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0938
United Utilities | LEIGH STW | LEIGH WwTW | 016920134 | 16920134 | SO | Inlet SO at WwTW | SJ6581099000 | GB112069060760 | Pennington Brook (Glaze) | PENNINGTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 100 | [5 empty] | UUG0939
United Utilities | WIGAN ROAD/SIDDELEY STREET CSO | Wigan Road/Siddeley Street CSO | 016993668 | WIG0064 | SO | SO on sewer network | SD6485000290 | GB112069060820 | Westleigh Brook | WESTLEIGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 75.78 | 45 | 42 | 4 (installed 2019) | 93.16 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0940
United Utilities | TWIST LANE/WESTLEIGH BRIDGE CSO | Twist Lane/Westleigh Bridge CSO | 01WIG0065 | WIG0065 | SO | SO on sewer network | SD6482000241 | GB112069060820 | Westleigh Brook | WESTLEIGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 37.03 | 41 | 16.8 | 5 (installed 2018) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0941
United Utilities | FIRS LANE/URMSTON STREET CSO | FIRS LANE / URMSTON STREET CSO | 01WIG0066 | WIG0066 | SO | SO on sewer network | SD6482000240 | GB112069060820 | Westleigh Brook | WESTLEIGH BROOK | N/A | N/A | Not Applicable | Dec 2023 | 159.73 | 65 |  | <1 yr (installed 2023) | 98.5577 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0942
United Utilities | WESTLEIGH ETHERSTONE MD CSO 508AP | Westleigh/Etherstone Main Drainage CSO | 016993705 | WIG0069 | SO | SO on sewer network | SJ6475099780 | GB112069060820 | Westleigh Brook | WESTLEIGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 29.57 | 16 | 9.6 | 5 (installed 2018) | 100 | [5 empty] | UUG0943
United Utilities | WESTLEIGH PARK CSO 502ZF | Westleigh Park CSO | 016993633 | WIG0071 | SO | SO on sewer network | SD6498001600 | GB112069060820 | Westleigh Brook | WESTLEIGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 476.47 | 116 | 115.4 | 5 (installed 2018) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0944
United Utilities | MATHER LANE | Mather Lane CSO | 01WIG0080 | WIG0080 | SO | SO on sewer network | SJ6581099001 | GB112069060760 | Pennington Brook (Glaze) | PENNINGTON BROOK | N/A | N/A | Not Applicable | Dec 2023 | 3499.83 | 153 |  | <1 yr (installed 2023) | 93.6782 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0945
United Utilities | HIGH BRIDGE COMBINED SEWER OVERFLOW | HIGH BRIDGE CSO | 01WIG0081 | WIG0081 | SO | SO on sewer network | SJ6715099750 | GB112069060810 | Bedford Brook | BEDFORD BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0946
United Utilities | PARK LANE CSO 50098 | Park Lane CSO | 016993708 | WIG0082 | SO | SO on sewer network | SJ6725099700 | GB112069060810 | Bedford Brook | BEDFORD BROOK TRIB GLAZE BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1603.09 | 120 | 79.6 | 5 (installed 2018) | 86.01 | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0947
United Utilities | York Avenue CSO | York Avenue CSO | 16993565 | WIG0086 | SO | SO on sewer network | SD6872902584 | GB112069060810 | Hindsford Brook | HINDSFORD BROOK/SHAKERLEY BROO | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected |  |  | 94 | 3 (installed 2020) | 0 | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0948
United Utilities | York Avenue CSO | York Avenue CSO | 16993565 | WIG0086 | SO | SO on sewer network | SD6872902584 | GB112069060810 | Shakerley Brook | HINDSFORD BROOK/SHAKERLEY BROO | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 23.85 | 32 | 32.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG0949
United Utilities | FACTORY ST/CHARLES ST CSO | Factory Street/Charles Street CSO, Leigh | 016993530 | WIG0087 | SO | SO on sewer network | SD6862002140 | GB112069060810 | Bedford Brook | HINDSFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.6 | 2 | 5.75 | 4 (installed 2019) | 100 | [5 empty] | UUG0950
United Utilities | CENTRAL PUMPING STATION | Central Pumping Station | 01WIG0100 | WIG0100 | SO | Storm discharge at pumping station | SD6689000000 | GB112069060810 | Bedford Brook | BEDFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 22.24 | 17 | 26.4 | 5 (installed 2018) | 99.96 | [5 empty] | UUG0951
United Utilities | QUEENSWAY PS | Higher Folds (Queensway) PS | 01WIG0101 | WIG0101 | SO | Storm discharge at pumping station | SD6746000370 | GB112069060810 | Bedford Brook | PEN LEACH BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 22.81 | 8 | 11.3333 | 3 (installed 2020) | 99.85 | [5 empty] | UUG0952
United Utilities | KIRKHALL LANE CSO | Kirkhall Lane CSO | 01WIG0107 | WIG0107 | SO | SO on sewer network | SD6495001370 | GB112069060820 | Westleigh Brook | Westleigh Brook | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 282.27 | 81 | 69 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0953
United Utilities | KIRKHALL LANE/VICTORIA STREET CSO | Kirkhall Lane/Victoria Street CSO | EPRQB3595RE | WIG0141 | SO | SO on sewer network | SD6501001510 | GB112069060820 | Westleigh Brook | WESTLEIGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 58.5 | 59 | 54.25 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0954
United Utilities | TYLDESLEY CSO | Tyldesley Western CSO | 016920502 | WIG0151 | SO | SO on sewer network | SD6816002000 | GB112069061100 | Astley Brook (Mersey) | HINDSFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 444.2 | 61 | 53.75 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0955
United Utilities | MILL LANE LEIGH CSO 50079 | Mill Lane (Leigh) CSO | 01WIG0198 | WIG0198 | SO | SO on sewer network | SJ6690099950 | GB112069060810 | Bedford Brook | BEDFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 27.33 | 32 | 26.4 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0956
United Utilities | MANCHESTER RD/PARK LANE CSO | Manchester Road/Park Lane CSO | 01WIG0199 | WIG0199 | SO | SO on sewer network | SJ6721099720 | GB112069060810 | Bedford Brook | BEDFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 449.93 | 85 | 47.25 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0957
United Utilities | LOVERS LANE/LEIGH ROAD CSO (50080) | Lovers Lane/Leigh Road CSO | 016993101 | WIG0200 | SO | SO on sewer network | SD6629002300 | GB112069060810 | Bedford Brook | COLLIER BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 211.71 | 73 | 45 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0958
United Utilities | FULWELL AVENUE CSO | Fulwell Avenue CSO | 016982785 | WIG0205 | SO | SO on sewer network | SD6815002000 | GB112069060810 | Bedford Brook | HINDSFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 616.35 | 54 | 43 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0959
United Utilities | GLOUCESTER ST CSO | Gloucester street CSO | 016982786 | WIG0207 | SO | SO on sewer network | SD6686003290 | GB112069060810 | Bedford Brook | COLLIER BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1360.67 | 110 | 105.75 | 4 (installed 2019) | 85.49 | Comms failure / issue | Scheduled | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0960
United Utilities | LEIGH SSO | Green Lane Leigh | 016920277 | WIG0211 | SO | SO on sewer network | SD6743000380 | GB112069060810 | Bedford Brook | PEN LEACH BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0961
United Utilities | NEWLANDS ROAD CSO | Newlands Road CSO | 016983326 | WIG0230 | SO | SO on sewer network | SJ6573099180 | GB112069060760 | Pennington Brook (Glaze) | PENNINGTON BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 7.9 | 8 | 4.6667 | 3 (installed 2020) | 75.33 | Comms failure / issue | Resolved - January after reporting year |  |  |  | UUG0962
United Utilities | SHAKERLEY ROAD NO2 CSO | Shakerley Road No 2 CSO | 016983325 | WIG0233 | SO | SO on sewer network | SD6869002250 | GB112069060810 | Bedford Brook | SHAKERLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 162.7 | 25 | 41 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0963
United Utilities | ELLESMERE STREET CSO | Ellesmere Street CSO | 016983324 | WIG0234 | SO | SO on sewer network | SD6875102302 | GB112069060810 | Bedford Brook | SHAKERLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 25.03 | 30 | 30.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0964
United Utilities | Primrose Street/Ellesmere Street CSO | Primrose Street/Ellesmere Street CSO | 016983323 | WIG0235 | SO | SO on sewer network | SD6875102302 | GB112069060810 | Bedford Brook | SHAKERLEY BROOK | N/A | N/A | Not Applicable | Dec 2023 | 36.1 | 37 |  | <1 yr (installed 2023) | 99.52 | [5 empty] | UUG0965
United Utilities | KIRIBATI WAY CSO | Kiribati Way CSO | 016983320 | WIG0238 | SO | SO on sewer network | SD6503000870 | GB112069060820 | Westleigh Brook | WESTLEIGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.5 | 2 | 1 | 3 (installed 2020) | 100 | [5 empty] | UUG0966
United Utilities | STIRLING CLOSE CSO 508NA | Stirling Close CSO | 016993846 | WIG0244 | SO | SO on sewer network | SD6790000450 | GB112069060810 | Bedford Brook | COLLING LANE BROOK, PEN LEACH | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 66.47 | 16 | 12.8 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0967
United Utilities | LAWTON GATE WWTW | LAWTON GATE WwTW | 016810085 | 16810085 | SO | Inlet SO at WwTW | SJ8090056490 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | KIDSGROVE STREAM | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 74.5 | 30 | 29.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0968
United Utilities | LAWTON GATE WWTW | LAWTON GATE WwTW | 016810085 | 16810085 | ST | Storm tank at WwTW | SJ8090056490 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | KIDSGROVE STREAM | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 672.53 | 48 | 46.5 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0969
United Utilities | THURLWOOD NO.1 PS | Thurlwood No 1 PS | 016881933 | CON0067 | SO | Storm discharge at pumping station | SJ8005057690 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | TRENT AND MERSEY CANAL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 163.3 | 39 | 31.25 | 4 (installed 2019) | 99.98 | [5 empty] | UUG0970
United Utilities | CHESTNUT AVENUE PS | Chestnut Avenue PS | 016881932 | CON0086 | SO | Storm discharge at pumping station | SJ8030057470 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | TRENT & MERSEY CANAL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 45.6 | 44 | 33.6667 | 3 (installed 2020) | 100 |  |  | Data collection - EDM non-representative location | Scheduled |  | UUG0971
United Utilities | LAVERSDALE WWTW | LAVERSDALE WWTW | 17670067 | 17670067 | SO | Inlet SO at WwTW | NY4738062330 | GB102076073970 | Brunstock Beck | Brunstock Beck | N/A | N/A | Not Applicable | Dec 2023 | 0 | 0 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0972
United Utilities | LANGWATHBY WWTW | LANGWATHBY WwTW | 017670066 | 17670066 | ST | Storm tank at WwTW | NY5590034100 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1148.56 | 65 | 81.25 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0973
United Utilities | SKIRWITH HALL CSO | Skirwith Hall Combined Sewer Overflow | 01EDE0003 | EDE0003 | SO | SO on sewer network | NY6134032480 | GB102076073800 | Briggle Beck | SKIRWITH BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 5.27 | 9 | 13.25 | 4 (installed 2019) | 100 | [5 empty] | UUG0974
United Utilities | LANGWATHBY COMBINED SEWER OVERFLOW | Langwathby CSO | EPRRP3420XG | EDE0120 | SO | Storm discharge at pumping station | NY5652534220 | GB102076073800 | Briggle Beck | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 408.69 | 93 | 96.75 | 4 (installed 2019) | 99.95 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG0975
United Utilities | SKIRWITH PS (WAS WWTW) | Skirwith PS | EPRFP3523KN | EDE0121 | SO | Storm discharge at pumping station | NY6062032750 | GB102076073800 | Briggle Beck | BRIGGLE BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 14.49 | 5 | 12.75 | 4 (installed 2019) | 99.84 | [5 empty] | UUG0976
United Utilities | WINSKILL PUMPING STATION | Winskill PS | EPRFP3523XL | EDE0122 | SO | Storm discharge at pumping station | NY5756034680 | GB102076073800 | Briggle Beck | BRIGGLE BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 8.63 | 5 | 4.5 | 4 (installed 2019) | 99.87 | [5 empty] | UUG0977
United Utilities | ELTERWATER PUMPING STATION | Elterwater pumping station (ELTER) (LAK0025) | 01LAK0025 | LAK0025 | SO | Storm discharge at pumping station | NY3279004720 | GB112073071120 | Great Langdale Beck | GREAT LANGDALE BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 996 | 41 | 42 | 5 (installed 2018) | 99.95 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0978
United Utilities | LANCASTER WWTW LANCA | Lancaster WwTW | 017270050 | 17270050 | ST | Storm tank at WwTW | SD4570058710 | GB531207212100 | LUNE | LUNE ESTUARY | N/A | Morecambe North; Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 603.71 | 46 | 40.8333 | 6 (installed 2017) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0979
United Utilities | LEA GATE PUMPING STATION | Lea Gate PS | 017180631 | PRE0113 | SO | Storm discharge at pumping station | SD4789030020 | 176 |  | SAVICK BK, TRIB OF RIBBLE EST | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 105.96 | 40 | 38.6 | 5 (installed 2018) | 99.86 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG0980
United Utilities | HAWTHORN CRESCENT CSO | Hawthorn Crescent CSO | NPSWQD010099 | PRE0122 | SO | SO on sewer network | SD4948029980 | 176 |  | RIVER RIBBLE | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 2.73 | 11 | 20 | 7 (installed 2016) | 99.99 | [5 empty] | UUG0981
United Utilities | PRESTON NETWORK TERMINAL PUMPING ST | Preston Network Terminal Pumping Station (Site ID HOWCK) (PRE0125) | EPRMB3990NU | PRE0125 | SO | Storm discharge at pumping station | SD5037729025 | 175 |  | TIDAL RIVER RIBBLE | N/A | St Annes | Not Applicable | Commissioned in 2017 - full year data expected | 67.09 | 12 | 15.3333 | 6 (installed 2017) | 99.79 | [5 empty] | UUG0982
United Utilities | RAILWAY FARM CSO 25051 | Railway Farm Combined Sewer Overflow (Site ID 25051) (LAN0031) | 017220120 | LAN0031 | SO | SO on sewer network | SD4808055240 | GB112072065900 | Conder | RIVER CONDOR | N/A | Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 76.5 | 17 | 22 | 6 (installed 2017) | 100 | [5 empty] | UUG0983
United Utilities | WATERY LANE DOUGLAS ST CSO PRE0110 | Watery Lane/Douglas Street CSO | 017180544 | PRE0110 | SO | SO on sewer network | SD5220029870 | 176 |  | CHAIN CAUL WARD STORM | N/A | N/A | Not Applicable | Dec 2023 | 9.93 | 4 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG0984
United Utilities | OXCLIFFE RD PS NO 1 & EO TO OVERTON | Oxcliffe Road Pumping Station (Site ID 25006) (LAN0028) | 01LAN0028 | LAN0028 | SO | Storm discharge at pumping station | SD4476061080 | GB531207212100 | LUNE | RIVER LUNE ESTUARY | N/A | Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 10.87 | 25 | 4.1667 | 6 (installed 2017) | 99.97 | [5 empty] | UUG0985
United Utilities | HEYSHAM VILLAGE PUMPING STATION | Heysham Village PS | 017370153 | LAN0043 | SO | Storm discharge at pumping station | SD4100061990 | GB641211171000 | Morecambe Bay | MORECAMBE BAY | N/A | N/A | Not Applicable | Commissioned pre-2016 - full year data expected | 0.11 | 1 | 0.125 | 8 (installed 2015) | 100 | [5 empty] | UUG0986
United Utilities | RAMPARTS CSO 25075 | Ramparts CSO | 017280425 | LAN0072 | SO | SO on sewer network | SD4792062410 | GB531207212100 | LUNE | RIVER LUNE ESTUARY | N/A | Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 1478.52 | 62 | 15 | 6 (installed 2017) | 100 |  |  | Data collection - EDM non-representative location | Resolved - Dec | Other investigation - non-WINEP/Green Recovery | UUG0987
United Utilities | RIVERSIDE ROAD CSO | Riverside Road CSO | 01SRI0002 | SRI0002 | SO | SO on sewer network | SD5307028190 | 175 |  | RIVER RIBBLE | N/A | Southport; St Annes Pier; St. Annes North; Blackpool South | Not Applicable | Commissioned in 2018 - full year data expected | 10.1 | 3 | 5.4 | 5 (installed 2018) | 99.99 | [5 empty] | UUG0988
United Utilities | LANCASTER BUS STATION CSO | Lancaster Bus Station CSO | 017280277 | LAN0077 | SO | SO on sewer network | SD4770061870 | GB112069061161 | Lune | MILL RACE | N/A | Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 34.09 | 17 | 12.6667 | 6 (installed 2017) | 99.89 | [5 empty] | UUG0989
United Utilities | VALLEY ROAD PUMPING STATION | Valley Road PS | 017160300 | SRI0003 | SO | Storm discharge at pumping station | SD5281028450 | 175 |  | RIVER RIBBLE | N/A | Southport; St Annes Pier; St. Annes North; Blackpool South | Not Applicable | Commissioned in 2018 - full year data expected | 15.55 | 8 | 18.4 | 5 (installed 2018) | 99.97 | [5 empty] | UUG0990
United Utilities | COP LANE CSO | Cop Lane CSO | 017190853 | SRI0031 | SO | SO on sewer network | SD5223028130 | 175 |  | TRIBOF RIVER RIBBLE | N/A | St Annes | Not Applicable | Commissioned in 2018 - full year data expected | 28.63 | 5 | 3.6 | 5 (installed 2018) | 100 | [5 empty] | UUG0991
United Utilities | DAMSIDE | Damside Screening Chamber | 017280381 | LAN0113 | SO | SO on sewer network | SD4757062060 | GB531207212100 | LUNE | RIVER LUNE ESTUARY | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG0992
United Utilities | OWEN ROAD COMBINED SEWER OVERFLOW | Owen Road CSO | 017280424 | LAN0116 | SO | SO on sewer network | SD4788062360 | GB531207212100 | LUNE | RIVER LUNE ESTUARY | N/A | Morecambe South | Not Applicable | Commissioned in 2017 - full year data expected | 169.5 | 17 | 67.6667 | 6 (installed 2017) | 52.8 | Comms failure / issue | Resolved - January after reporting year | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0993
United Utilities | KNUTSFORD WWTW | KNUTSFORD WwTW | 016910007 | 16910007 | ST | Storm tank at WwTW | SJ7680079910 | GB112069061340 | Birkin Brook - Source to Mobberley Brook | BIRKIN BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2138.67 | 153 | 186 | 4 (installed 2019) | 99.87 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0994
United Utilities | BEXTON ROAD COMBINED SEWER OVERFLOW | Bexton Road CSO | 01MAC0001 | MAC0001 | SO | SO on sewer network | SJ7320077500 | GB112068060410 | Smoker Brook (Gale Brook to Wincham Brook) | SERPENTINE WATER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 87.43 | 67 | 76.4 | 5 (installed 2018) | 99.99 |  |  | Data collection - EDM non-representative location | N/A - Ongoing investigation | U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP or Green Recovery | UUG0995
United Utilities | ST JOHNS WOOD CSO 272S9 | St Johns Road CSO | 01MAC0026 | MAC0026 | SO | SO on sewer network | SJ7692079330 | GB112069061340 | Birkin Brook - Source to Mobberley Brook | BIRKIN BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 109.67 | 70 | 121.2 | 5 (installed 2018) | 99.76 |  |  | Data collection - EDM non-representative location | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG0996
United Utilities | MOBBERLEY RD CSO | Mobberley Road Combined Sewer Overflow (Site ID 272GZ) (MAC0122) | 016892553 | MAC0122 | SO | SO on sewer network | SJ7684079530 | GB112069061340 | Birkin Brook - Source to Mobberley Brook | BIRKIN BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 58.07 | 74 | 68.75 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG0997
United Utilities | KNUTSFORD MAIN PUMPING STATION | Knutsford Main PS | 01MAC0144 | MAC0144 | SO | Storm discharge at pumping station | SJ7548078730 | GB112069061340 | Birkin Brook - Source to Mobberley Brook | MOOR POOL | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 15.72 | 9 | 10.5 | 6 (installed 2017) | 100 | [5 empty] | UUG0998
United Utilities | KIRKOSWALD STW | KIRKOSWALD WwTW | 017670065 | 17670065 | ST | Storm tank at WwTW | NY5471041200 | GB102076073940 | Eden - Eamont to tidal | TRIB RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 20.56 | 15 | 10.75 | 4 (installed 2019) | 99.92 | [5 empty] | UUG0999
United Utilities | CROFT CLOSE COMBINED SEWER OVERFLOW | The College CSO | 01EDE0007 | EDE0007 | SO | SO on sewer network | NY5534041150 | GB102076073840 | Raven Beck | RAVEN BECK,TRIB OF RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 27.77 | 53 | 53 | 4 (installed 2019) | 97.7 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1000
United Utilities | BEHIND LAGER STORE CSO (174LJ) | CSO behind Lager's Store | 01EDE0022 | EDE0022 | SO | SO on sewer network | NY5471039590 | GB102076073940 | Eden - Eamont to tidal | HARROW BECK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 29.57 | 53 | 62.3333 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1001
United Utilities | KIRKOSWALD VILLAGE PUMPING STATION | Kirkoswald PS | 01EDE0067 | EDE0067 | SO | Storm discharge at pumping station | NY5553041150 | GB102076073840 | Raven Beck | RAVEN BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2.59 | 10 | 8.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1002
United Utilities | LAZONBY PS AND CSO | Lazonby PS and CSO | 017670241 | EDE0073 | SO | Storm discharge at pumping station | NY5516039980 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 91.99 | 81 | 76.5 | 4 (installed 2019) | 99.89 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1003
United Utilities | KIRKLAND STW | KIRKLAND WwTW | 017470029 | 17470029 | SO | Inlet SO at WwTW | NY0733017430 | GB112074070010 | Ehen (upper including Liza) | HAWES GILL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 24.6 | 40 | 55 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1004
United Utilities | KIRKBY THORE PS | Kirkby Thore PS | 017680336 | EDE0087 | SO | Storm discharge at pumping station | NY6364025290 | GB102076070930 | Trout Beck | TROUT BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 148.98 | 39 | 44.75 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1005
United Utilities | KIRKBY STEPHEN WWTW | Kirkby Stephen WwTW | 017670013 | 17670013 | ST | Storm tank at WwTW | NY7717010460 | GB102076070590 | Eden - headwaters to Scandal Beck | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 3225.82 | 172 | 165.75 | 4 (installed 2019) | 92.05 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1006
United Utilities | KIRKBY STEPHEN WWTW | Kirkby Stephen WwTW | 017670013 | 17670013 | SO | Inlet SO at WwTW | NY7717010460 | GB102076070590 | Eden - headwaters to Scandal Beck | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1423.89 | 135 | 33.75 | 4 (installed 2019) | 92.05 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1007
United Utilities | WINTON PUMPING STATION | Winton PS | 017670197 | EDE0064 | SO | Storm discharge at pumping station | NY7760010530 | GB102076070590 | Eden - headwaters to Scandal Beck | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2091.66 | 168 | 166.5 | 4 (installed 2019) | 99.93 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1008
United Utilities | STENKRITH BRIDGE SSO | Stenkrith Bridge CSO | 017680271 | EDE0076 | SO | SO on sewer network | NY7730007470 | GB102076070590 | Eden - headwaters to Scandal Beck | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 148.63 | 23 | 25 | 4 (installed 2019) | 100 | [5 empty] | UUG1009
United Utilities | FRANKS BRIDGE CSO (171UZ) | Franks Bridge SSO | 017680272 | EDE0077 | SO | SO on sewer network | NY7764008720 | GB102076070590 | Eden - headwaters to Scandal Beck | RIVER EDEN VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 482.37 | 90 | 67.3333 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1010
United Utilities | KIRKBY LONSDALE STW | KIRKBY LONSDALE WwTW | 017270006 | 17270006 | SO | Inlet SO at WwTW | SD6152077880 | GB112072071690 | Lune - conf Rawthey to conf Greta | RIVER LUNE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 69.09 | 60 | 56 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1011
United Utilities | KIRKBY LONSDALE STW | KIRKBY LONSDALE WwTW | 017270006 | 17270006 | ST | Storm tank at WwTW | SD6152077880 | GB112072071690 | Lune - conf Rawthey to conf Greta | RIVER LUNE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 299.25 | 61 | 65 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1012
United Utilities | RAVENGLASS STW | RAVENGLASS WwTW | 017470074 | 17470074 | ST | Storm tank at WwTW | SD0853096020 | 186 |  | RIVER ESK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 481.27 | 38 | 107.8 | 5 (installed 2018) | 100 |  |  | Performance - Asset power failure | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1013
United Utilities | ROA ISLAND PUMPING STATION | Roa Island PS | 017480366 | BRW0102 | SO | Storm discharge at pumping station | SD2318164600 | 342 |  | PIEL CHANNEL | 116 Walney | Walney | Not Applicable | Commissioned in 2016 - full year data expected | 105.61 | 53 | 88 | 7 (installed 2016) | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1014
United Utilities | ROCKCLIFFE PUMPING STATION | Rockcliffe Pumping Station (Site ID RCKCL) (CAR0027) | 017680414 | CAR0027 | SO | Storm discharge at pumping station | NY3578061630 | 89 |  | ROCKCLIFFE BECK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 332.6 | 76 | 74.8333 | 6 (installed 2017) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1015
United Utilities | HARDWICK ROADCSO | Hardwick Street CSO | 01HAL0008 | HAL0008 | SO | SO on sewer network | SJ5253083240 | 169 |  | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 25.5 | 15 | 34.75 | 4 (installed 2019) | 99.99 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG1016
United Utilities | KINGSLEY STW | KINGSLEY WwTW | 016810084 | 16810084 | ST | Storm tank at WwTW | SJ5677074520 | GB112068060550 | Crowton Brook | TRIB CROWTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 960.59 | 81 | 60.25 | 4 (installed 2019) | 98.47 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1017
United Utilities | OFF RODDY LANE CSO (472O5) | Off Roddy Lane CSO | 01VRY0063 | VRY0063 | SO | SO on sewer network | SJ5676074510 | GB112068060550 | Crowton Brook | TRIB OF CROWTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 214.63 | 84 | 78.6667 | 3 (installed 2020) | 99.98 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1018
United Utilities | OFF WELL LANE KINGSLEY CSO (472JN) | Off Well Lane Kingsley CSO | 01VRY0064 | VRY0064 | SO | SO on sewer network | SJ5528074740 | GB112068060550 | Crowton Brook | KINGSLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 3.7 | 15 | 9 | 3 (installed 2020) | 99.99 | [5 empty] | UUG1019
United Utilities | KIDSGROVE WWTW | KIDSGROVE WwTW | 016810083 | 16810083 | ST | Storm tank at WwTW | SJ8284055210 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | KIDSGROVE STREAM WHEELOCK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 205.1 | 14 | 12 | 3 (installed 2020) | 99.4 | [5 empty] | UUG1020
United Utilities | LIVERPOOL RD CSO | Liverpool Road CSO | 016881976 | NEW0010 | SO | SO on sewer network | SJ8315054910 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | KIDSGROVE STREAM | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 442.4 | 77 | 115.3333 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1021
United Utilities | ROOKERY CSO | Rookery CSO (29010) (NEW0038) | 016810825 | NEW0038 | SO | SO on sewer network | SJ8484055630 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | ROOKERY BROOK TRIB KIDSGROVE S | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 168.61 | 23 | 47.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1022
United Utilities | TALKE INDUSTRIAL EST CSO | Talke Industrial Estate Combined Sewer Overflow (Site ID 292UG) (NEW0037) | 016881957 | NEW0037 | SO | SO on sewer network | SJ8205052251 | GB112068074630 | Valley Brook (Source to Englesea Brook) | TRIB VALLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0 | 4 (installed 2019) | 100 | [5 empty] | UUG1023
United Utilities | KESWICK STW | KESWICK WwTW | 017570044 | 17570044 | ST | Storm tank at WwTW | NY2487224952 | GB112075073561 | Derwent US Bassenthwaite Lake | RIVER DERWENT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1066.77 | 78 | 81.6 | 5 (installed 2018) | 99.88 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1024
United Utilities | RAWNSLEY HALL PUMPING STATION | Rawnsley Hall PS (AKA Greta Grove) | 017580420 | ALL0021 | SO | Storm discharge at pumping station | NY2617023680 | GB112075073561 | Derwent US Bassenthwaite Lake | THE RIVER GRETA | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 42.04 | 60 | 49.6667 | 6 (installed 2017) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1025
United Utilities | A591 BUS SHELTER CSO 021BY | A591/Bus Shelter CSO | 01ALL0026 | ALL0026 | SO | SO on sewer network | NY2587025070 | GB112075073561 | Derwent US Bassenthwaite Lake | APPLETHWAITE GILL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 551.9 | 72 | 79.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1026
United Utilities | BRAITHWAITE WW PUMPING STATION | Braithwaite Ww PS | 01ALL0056 | ALL0056 | SO | Storm discharge at pumping station | NY2365024400 | GB112075070440 | Newlands Beck | HALLGARTH BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1434.98 | 120 | 115.4 | 5 (installed 2018) | 100 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1027
United Utilities | THICK RIGGS CSO (022UY) | THICK RIGGS CSO | 01ALL0024 | ALL0024 | SO | SO on sewer network | NY2508023860 | GB112075073561 | Derwent US Bassenthwaite Lake | RIVER DERWENT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.13 | 1 | 1.2 | 5 (installed 2018) | 100 | [5 empty] | UUG1028
United Utilities | PORTINSCALE SEWAGE PUMPING STATION | Portinscale SPS | 01ALL0088 | ALL0088 | SO | Storm discharge at pumping station | NY2465023950 | GB112075070440 | Newlands Beck | POW BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 561.16 | 106 | 141 | 5 (installed 2018) | 99.91 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1029
United Utilities | LATTINGS CLOSE CSO 028NF | Lattrigg Close | 017580252 | ALL0095 | SO | SO on sewer network | NY2758023890 | GB112075073561 | Derwent US Bassenthwaite Lake | RIVER GRETA | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0.43 | 5 | 8.5 | 6 (installed 2017) | 100 | [5 empty] | UUG1030
United Utilities | PENRITH RD | Penrith Road | 01ALL0070 | ALL0070 | SO | SO on sewer network | NY2724023660 | GB112075073561 | Derwent US Bassenthwaite Lake | RIVER GRETA | N/A | N/A | Not Applicable | Dec 2023 | 22.63 | 6 |  | <1 yr (installed 2023) | 98.0583 | [5 empty] | UUG1031
United Utilities | KENDAL WASTE WATER TREATMENT WORKS | KENDAL WwTW | 017370100 | 17370100 | SO | Inlet SO at WwTW | SD5170090790 | GB112073071460 | Kent - conf Sprint to tidal | THE RIVER KENT | N/A | N/A | Not Applicable | Commissioned in 2021 - full year data expected | 439.47 | 62 | 39.5 | 2 (installed 2021) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1032
United Utilities | KENDAL WASTE WATER TREATMENT WORKS | KENDAL WwTW | 017370100 | 17370100 | ST | Storm tank at WwTW | SD5170090790 | GB112073071460 | Kent - conf Sprint to tidal | THE RIVER KENT | N/A | N/A | Not Applicable | Commissioned in 2021 - full year data expected | 822.29 | 69 | 44.5 | 2 (installed 2021) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1033
United Utilities | SEDGWICK PUMPING STATION | Sedgewick PS | 017370060 | LAK0091 | SO | Storm discharge at pumping station | SD5083087230 | GB112073071460 | Kent - conf Sprint to tidal | RIVER KENT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 51.3 | 38 | 7.6 | 5 (installed 2018) | 92.27 | [5 empty] | UUG1034
United Utilities | KABER WASTEWATER TREATMENT WORKS | KABER WwTW | 017670011 | 17670011 | SO | Inlet SO at WwTW | NY7953111665 | GB102076070620 | Belah (lower) | POPPING BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 429.44 | 64 | 61.25 | 4 (installed 2019) | 100 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1035
United Utilities | IRLAM WASTEWATER TREATMENT WORKS | IRLAM WwTW | 016940133 | 16940133 | SO | Inlet SO at WwTW | SJ7018092020 | GB112069061420 | Glaze | RIVER GLAZE (GLAZE BROOK) | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 225.9 | 73 | 68 | 3 (installed 2020) | 100 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1036
United Utilities | IRLAM WASTEWATER TREATMENT WORKS | IRLAM WwTW | 016940133 | 16940133 | ST | Storm tank at WwTW | SJ7018092020 | GB112069061420 | Glaze | RIVER GLAZE (GLAZE BROOK) | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1329.21 | 130 | 148 | 3 (installed 2020) | 100 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1037
United Utilities | LORDS STREET/LIVERPOOL ROAD CSO | LORDS STREET / LIVERPOOL ROAD CSO | 01SAL0015 | SAL0015 | SO | SO on sewer network | SJ7119091820 | GB112069061011 | Mersey/ Manchester Ship Canal (Irwell/Manchester Ship Canal to B | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 47.83 | 50 | 61 | 5 (installed 2018) | 97.22 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1038
United Utilities | FAIRHILLS ROAD CSO (37002) | FAIRHILLS ROAD CSO | 01SAL0023 | SAL0023 | SO | SO on sewer network | SJ7266093780 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 22.1 | 26 | 21.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG1039
United Utilities | LORDS STREET/FIR STREET CSO | LORDS STREET / FIR STREET CSO | 01SAL0049 | SAL0049 | SO | SO on sewer network | SJ6992092520 | GB112069061420 | Glaze | RIVER GLAZE | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1040
United Utilities | GLAZEBROOK LANE CSO IN FIELD | Glazebrook Lane CSO | 01WAR0040 | WAR0040 | SO | SO on sewer network | SJ7019091940 | GB112069061420 | Glaze | GLAZE BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 10.17 | 10 | 6 | 3 (installed 2020) | 99.99 | [5 empty] | UUG1041
United Utilities | ST HELENS CLOSE CSO | ST HELENS CLOSE CSO | 01WAR0047 | WAR0047 | SO | SO on sewer network | SJ7015091300 | GB112069061420 | Glaze | RIVER GLAZE VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 497.17 | 88 | 102.6667 | 3 (installed 2020) | 88.46 | Comms failure / issue | Resolved - January after reporting year | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1042
United Utilities | IREBY WWTW | IREBY WwTW | 017570071 | 17570071 | SO | Inlet SO at WwTW | NY2405039260 | GB112075073630 | Ellen (upper) | RIBER ELLEN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 331.36 | 109 | 99 | 3 (installed 2020) | 100 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1043
United Utilities | INGLETON STW | INGLETON WwTW | 017260005 | 17260005 | ST | Storm tank at WwTW | SD6868072620 | GB112072071610 | Greta | RIVER GRETA | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 3848.87 | 201 | 190.8 | 5 (installed 2018) | 100 |  |  | Performance - Infiltration | Scheduled | Stage 1c: Confirmed "hydraulic issue" | UUG1044
United Utilities | HYNDBURN WWTW HYNBD | Hyndburn WwTW | 017160008 | 17160008 | ST | Storm tank at WwTW | SD7562033370 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER (RIBBLE) | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 808.17 | 71 | 77.6 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1045
United Utilities | STATION ROAD (PALIHAM) CSO | Station Road (Padiham) CSO | 01BUR0018 | BUR0018 | SO | SO on sewer network | SD7937033870 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 49.53 | 72 | 72 | 3 (installed 2020) | 94.43 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1046
United Utilities | LIVERPOOL ROAD CSO (088NF) | Liverpool Road (Burnley) CSO | 01BUR0012 | BUR0012 | SO | SO on sewer network | SD8219032540 | GB112071065080 | Green Brook | RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 99.99 | [5 empty] | UUG1047
United Utilities | INSKIP STREET (082AK) CSO | INSKIP STREET CSO | 01BUR0022 | BUR0022 | SO | SO on sewer network | SD7939033840 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 206.27 | 87 | 78 | 3 (installed 2020) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1048
United Utilities | OPP 76 BURNLEY ROAD CSO | OPP 76 BURNLEY ROAD CSO | 01BUR0021 | BUR0021 | SO | SO on sewer network | SD7960033720 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 131.1 | 88 | 29.3333 | 3 (installed 2020) | 96.17 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1049
United Utilities | SLADE LANE CSO | SLADE LANE CSO | 01BUR0025 | BUR0025 | SO | SO on sewer network | SD7915034490 | GB112071065490 | Calder - Pendle Water to conf Ribble | DEAN CLOUGH RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 33.73 | 24 | 24.75 | 4 (installed 2019) | 100 | [5 empty] | UUG1050
United Utilities | ALTHAM OUTFALL (FENNYFOLD) CSO | Altham Outfall CSO | 017160089 | BUR0026 | SO | SO on sewer network | SD7883033050 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1381.31 | 153 | 97.6667 | 3 (installed 2020) | 79.32 | Capital / maintenance works affect EDM operation | N/A - Ongoing investigation | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1051
United Utilities | SHUTTLEWORTH STCALDER ST CSO | SHUTTLEWORTH STREET / CALDER STREET CSO | 01BUR0024 | BUR0024 | SO | SO on sewer network | SD7926033900 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0.25 | 4 (installed 2019) | 96.89 | [5 empty] | UUG1052
United Utilities | ADJACENT TO PADIHAM LEISURE CENTRE | Padiham Leisure Centre CSO | 017190925 | BUR0036 | SO | SO on sewer network | SD7912033690 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 102 | 43 | 43 | 3 (installed 2020) | 92.23 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1053
United Utilities | IN FRONT OF NO.19 BEAR STREET CSO | Bear Street CSO | NPSWQD010104 | BUR0037 | SO | SO on sewer network | SD8046033002 | GB112071065080 | Green Brook | SWEET CLOUGH TRIB GREEN BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 5.3333 | 3 (installed 2020) | 0.27 | Comms failure / issue | Resolved - January after reporting year |  |  |  | UUG1054
United Utilities | LEVANT MILL FOOTBRIDGE CSO (O82CV) | Levant Mill Footbridge CSO | 01BUR0027 | BUR0027 | SO | SO on sewer network | SD7958033440 | GB112071065080 | Green Brook | GREEN BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0.33333 | 3 (installed 2020) | 99.98 | [5 empty] | UUG1055
United Utilities | STOCKBRIDGE ROAD CSO (BUR0038) | Stockbridge Road Burnley CSO | EPRJB3895EB | BUR0038 | SO | SO on sewer network | SD7963933472 | GB112071065080 | Green Brook | GREEN BROOK | N/A | N/A | Not Applicable | Dec 2023 | 3290.1 | 183 |  | <1 yr (installed 2023) | 96.6184 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1056
United Utilities | Rishton Tank CSO | Rishton Tank CSO | 017160074 | HYN0003 | SO | SO on sewer network | SD7222030640 | GB112071065070 | Hyndburn Brook - Lower | LIVERPOOL & LEEDS CANAL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 136.08 | 80 | 66.6667 | 3 (installed 2020) | 97.13 |  |  | Data collection - EDM non-representative location | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1057
United Utilities | CLAYTON LE MOORS TANK CSO 22016 | Clayton-le-Moors Tank | 017160093 | HYN0004 | SO | SO on sewer network | SD7428031740 | GB112071065070 | Hyndburn Brook - Lower | HYNDBURN BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 367.12 | 79 | 72 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1058
United Utilities | ACCRINGTON SSO | Accrington CSO | 017160124 | HYN0005 | SO | SO on sewer network | SD7425029430 | GB112071065040 | Hyndburn | RIVER HYNDBURN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 578.32 | 124 | 88.6 | 5 (installed 2018) | 93.76 |  |  | Data collection - EDM non-representative location | Scheduled | Other investigation - non-WINEP/Green Recovery | UUG1059
United Utilities | TINKER BROOK CSO (22018) | Tinker Brook CSO | 017160120 | HYN0006 | SO | SO on sewer network | SD7416028380 | GB112071065050 | Hyndburn Brook - Upper | TINKER BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 44.04 | 37 | 38 | 3 (installed 2020) | 100 | [5 empty] | UUG1060
United Utilities | OSWALDTWISTLE CSO | Oswaldwistle CSO | 017160125 | HYN0008 | SO | SO on sewer network | SD7366028508 | GB112071065050 | Hyndburn Brook - Upper | WHITE ASH BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 273.12 | 81 | 68 | 3 (installed 2020) | 99.86 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1061
United Utilities | GREAT HARWOOD (HYNBURN RD)CSO 22017 | Great Harwood (Hyndbunr Rd) CSO | 017160127 | HYN0009 | SO | SO on sewer network | SD7470032330 | GB112071065070 | Hyndburn Brook - Lower | HYNDBURN BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 245.58 | 70 | 58 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1062
United Utilities | REAR OF 34 DINELY STREET CSO | Rear of 34 DINELY STREET CSO | 01HYN0023 | HYN0023 | SO | SO on sewer network | SD7452028880 | GB112071065040 | Hyndburn | RIVER HYNDBURN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.2 | 1 | 5 | 4 (installed 2019) | 100 | [5 empty] | UUG1063
United Utilities | CALDER, HUNCOAT INDUSTRIAL ESTATE | Huncoat Industrial Site | 01HYN0012 | HYN0012 | SO | SO on sewer network | SD7730130446 | GB112071065490 | Calder - Pendle Water to conf Ribble | CLOUGH BROOK | N/A | N/A | Not Applicable | Dec 2023 | 1 | 8 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1064
United Utilities | HILL STREET CSO | Hill Street CSO | 017190786 | HYN0027 | SO | SO on sewer network | SD7654026610 | GB112071065040 | Hyndburn | WOODNOOK WATER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.43 | 3 | 8.75 | 4 (installed 2019) | 94.43 | [5 empty] | UUG1065
United Utilities | PRIESTLEY CLOUGH CSO | PRIESTLY CLOUGH CSO | 01HYN0028 | HYN0028 | SO | SO on sewer network | SD7603027270 | GB112071065040 | Hyndburn | WOODNOOK WATER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 60.93 | 44 | 44.75 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1066
United Utilities | FAIRFIELD ST/STEVENSON ST EAST CSO | FAIRFIELD STREET / STEVENSON STREET EAST CSO | 01HYN0024 | HYN0024 | SO | SO on sewer network | SD7494028100 | GB112071065040 | Hyndburn | CULV SECTION OF TINKER BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.53 | 2 | 0.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1067
United Utilities | MELBOURNE STREET/WATER STREET CSO | MELBOURNE STREET / WATER STREET CSO | 01HYN0034 | HYN0034 | SO | SO on sewer network | SD7621028760 | GB112071065040 | Hyndburn | CULVERTED TRIB RIVER HYNDBURN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 12.25 | 4 (installed 2019) | 94.51 | [5 empty] | UUG1068
United Utilities | GRANGE LANE CSO | GRANGE LANE CSO | 01HYN0033 | HYN0033 | SO | SO on sewer network | SD7623028250 | GB112071065040 | Hyndburn | BROAD OAK WATER | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1069
United Utilities | 560 MANCHESTER ROAD CSO | 580 Manchester Road CSO | 01HYN0038 | HYN0038 | SO | SO on sewer network | SD7755026110 | GB112071065040 | Hyndburn | VIA CULVERT TO WOODNOOK WATER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.07 | 1 | 35.25 | 4 (installed 2019) | 100 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG1070
United Utilities | 20 RIBBLETON DRIVE CSO | 20 Ribbleton Drive CSO | 01HYN0035 | HYN0035 | SO | SO on sewer network | SD7614029920 | GB112071065490 | Calder - Pendle Water to conf Ribble | CLOUGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 11.53 | 26 | 6.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1071
United Utilities | OAKHURST AVENUE CSO | OAKHURST AVENUE CSO | 01HYN0040 | HYN0040 | SO | SO on sewer network | SD7716030060 | GB112071065490 | Calder - Pendle Water to conf Ribble | CULVERTEDTRIB. OF CLOUGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 11.03 | 10 | 9 | 4 (installed 2019) | 100 | [5 empty] | UUG1072
United Utilities | HUNCOAT PS | Nearer XXXXXX House Farm | 01HYN0050 | HYN0050 | SO | Storm discharge at pumping station | SD7695030690 | GB112071065490 | Calder - Pendle Water to conf Ribble | CLOUGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 35.7 | 12 | 16.8333 | 6 (installed 2017) | 99.98 | [5 empty] | UUG1073
United Utilities | SCOTT AVENUE/HURSTEAD STREET CSO | SCOTT AVENUE / HURSTHEAD STREET CSO | 01HYN0039 | HYN0039 | SO | SO on sewer network | SD7719026350 | GB112071065040 | Hyndburn | WOODNOOK WATER | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1074
United Utilities | REAR OF 489 MANCHESTER ROAD CSO | Rear of 489 Manchester Road CSO | 01HYN0053 | HYN0053 | SO | SO on sewer network | SD7688026530 | GB112071065040 | Hyndburn | WOODNOOK WATER VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.13 | 2 | 0.66667 | 3 (installed 2020) | 100 | [5 empty] | UUG1075
United Utilities | SABDEN CSO (342P9) | Sabden CSO | 01RIB0045 | RIB0045 | SO | SO on sewer network | SD7691036740 | GB112071065140 | Sabden Brook | Sabden Brook | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 37.43 | 10 | 23.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG1076
United Utilities | SIMONSTONE LANE CSO | Simonstone Lane CSO | EPRSB3396ES | RIB0050 | SO | SO on sewer network | SD7698033350 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 22.63 | 10 | 7.6667 | 3 (installed 2020) | 99.99 | [5 empty] | UUG1077
United Utilities | HYDE WASTEWATER TREATMENT WORKS | HYDE WwTW | 016940088 | 16940088 | SO | Inlet SO at WwTW | SJ9379094840 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 857.41 | 122 | 115.75 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1078
United Utilities | HYDE WASTEWATER TREATMENT WORKS | HYDE WwTW | 016940088 | 16940088 | ST | Storm tank at WwTW | SJ9379094840 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 177.2 | 31 | 45.75 | 4 (installed 2019) | 99.19 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1079
United Utilities | MEADOW LANE COMBINED SEWER OVERFLOW | Meadow Lane CSO | 01TAM0002 | TAM0002 | SO | SO on sewer network | SJ9338293069 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | Marple Brook | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 185.15 | 57 | 91 | 4 (installed 2019) | 99.45 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1080
United Utilities | SHERIDAN WAY CSO 44179 | Sheridan Way CSO | 01TAM0015 | TAM0015 | SO | SO on sewer network | SJ9271493544 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 22.97 | 27 | 56 | 5 (installed 2018) | 99.05 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1081
United Utilities | RAGLAN STREET CSO 44180 | Raglan Street CSO | 01TAM0020 | TAM0020 | SO | SO on sewer network | SJ9426094740 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1119.93 | 145 | 119.2 | 5 (installed 2018) | 89.91 | Comms failure / issue | Resolved - January after reporting year | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1082
United Utilities | VICTORIA ST/ACRE ST CSO (442WA) | Victoria Street/Acre Street Storm Overflow | 01TAM0062 | TAM0062 | SO | SO on sewer network | SJ9169094650 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | DENTON BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 29.13 | 39 | 39 | 3 (installed 2020) | 100 | [5 empty] | UUG1083
United Utilities | THORNLEY LANE SOUTH CSO 44019 | Thornley Lane South CSO | 016993676 | TAM0065 | SO | SO on sewer network | SJ9038094300 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | UNNAMED TRIB DENTON BRK SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 7.75 | 11 | 27 | 5 (installed 2018) | 99.74 | [5 empty] | UUG1084
United Utilities | TOWN LANE CIRCULAR ROAD CSO 44020 | Town Lane/Circular Road CSO | 01TAM0067 | TAM0067 | SO | SO on sewer network | SJ9192094851 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | DENTON BROOK TRIB RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 89.76 | 73 | 71.2 | 5 (installed 2018) | 74.78 | Sensor failure / issue | Resolved - Aug | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1085
United Utilities | SHOECROFT GARAGE SITE CSO | SHOECROFT GARAGE SITE CSO | 01TAM0068 | TAM0068 | SO | SO on sewer network | SJ9192094850 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | DENTON BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 44.93 | 58 | 50 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1086
United Utilities | HYDE ROAD (DENTON) CSO | HYDE ROAD Denton CSO | 01TAM0069 | TAM0069 | SO | SO on sewer network | SJ8900095910 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | River Tame | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 87.23 | 78 | 70.3333 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1087
United Utilities | WAKELING RD/STOCKPORT RD | Wakeling/Stockport Road CSO | 01TAM0070 | TAM0070 | SO | SO on sewer network | SJ9223093880 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | TRIBUTARY OF RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 2.03 | 6 | 9 | 3 (installed 2020) | 100 | [5 empty] | UUG1088
United Utilities | REAR OF KENNEDY WAY CSO | Rear of Kennedy Way CSO | 016993677 | TAM0073 | SO | SO on sewer network | SJ9158094450 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | DENTON BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 282.97 | 98 | 80.3333 | 3 (installed 2020) | 97.7 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1089
United Utilities | DUKINFIELD RD THROSTLE BANK ST CSO | Junction of Dukinfield Road and Throstle Bank Street combined sewer overflow (441SN) (TAM0079) | 01TAM0079 | TAM0079 | SO | SO on sewer network | SJ9417095610 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | UNNAMED TRIB RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 3.8 | 5 (installed 2018) | 96.86 | [5 empty] | UUG1090
United Utilities | SAWYER BROW/VICTORA STREET CSO | SAWYER BROW / VICTORIA STREET CSO | 01TAM0080 | TAM0080 | SO | SO on sewer network | SJ9560095900 | GB112069061280 | Wilson Brook | TRIBUTARY OF WILSON BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.17 | 1 | 1.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG1091
United Utilities | COMMERCIAL BROW CSO | COMMERCIAL BROW CSO | 01TAM0081 | TAM0081 | SO | SO on sewer network | SJ9554095390 | GB112069061280 | Wilson Brook | WILSON BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1092
United Utilities | CLOUGH END ROAD CSO 441KS | Clough End Road CSO | 01TAM0139 | TAM0139 | SO | SO on sewer network | SJ9864094380 | GB112069061050 | Etherow (Glossop Brook to Goyt) | HURST CLOUGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0.8 | 5 (installed 2018) | 100 | [5 empty] | UUG1093
United Utilities | CHAIN BAR LANE CSO | Chain Bar Lane CSO | 016993552 | TAM0140 | SO | SO on sewer network | SJ9869094790 | GB112069061050 | Etherow (Glossop Brook to Goyt) | HURST CLOUGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.75 | 1 | 4.5 | 4 (installed 2019) | 64.66 | Sensor failure / issue | Resolved - Oct |  |  |  | UUG1094
United Utilities | WELL ROW CSO 442XK | WELL ROW CSO | 01TAM0141 | TAM0141 | SO | SO on sewer network | SJ9928093690 | GB112069061050 | Etherow (Glossop Brook to Goyt) | RIVER ETHEROW | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 11.77 | 27 | 4.5 | 6 (installed 2017) | 99.98 | [5 empty] | UUG1095
United Utilities | BROADBOTTOM PUMPING STATION | Broadbottom PS | 016940167 | TAM0147 | SO | Storm discharge at pumping station | SJ9871093160 | GB112069061050 | Etherow (Glossop Brook to Goyt) | RIVER ETHEROW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.07 | 10 | 25 | 5 (installed 2018) | 100 | [5 empty] | UUG1096
United Utilities | MILVERTON AVENUE | Hattersley SSO | 01TAM0148 | TAM0148 | SO | SO on sewer network | SJ9717094480 | GB112069061280 | Wilson Brook | Wilson Brook | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1097
United Utilities | COMMERCIAL BROW CSO | Commercial Brow CSO | 016940359 | TAM0149 | SO | SO on sewer network | SJ9524095190 | GB112069061280 | Wilson Brook | GODLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 6 | 8 | 16 | 3 (installed 2020) | 99.94 | [5 empty] | UUG1098
United Utilities | OFF ST LAWRENCES ROAD CSO | Off St Lawrence Road CSO | 016982771 | TAM0151 | SO | SO on sewer network | SJ9335095090 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | TRIB OF RIVER TAME VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.3 | 1 | 2 | 3 (installed 2020) | 100 | [5 empty] | UUG1099
United Utilities | APETHORN LANE | Apethorn Lane | 016982688 | TAM0152 | SO | SO on sewer network | SJ9460093470 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | TRIB RIVER TAME | N/A | N/A | Not Applicable | Dec 2023 | 2347.73 | 198 |  | <1 yr (installed 2023) | 96.8182 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1100
United Utilities | MILL LANE COMBINED SEWER OVERFLOW | Mill Lane CSO | 016982772 | TAM0163 | SO | SO on sewer network | SJ9406094780 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2.04 | 10 | 10.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1101
United Utilities | OFF GIBRALTER LANE CSO | Off Gibralter Lane Haughton Green CSO | 016982692 | TAM0164 | SO | SO on sewer network | SJ9395093780 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 67.33 | 81 | 69.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1102
United Utilities | OFF MANOR ROAD CSO 442JF | Off Manor Road CSO | 016982693 | TAM0165 | SO | SO on sewer network | SJ9415094150 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 5.27 | 14 | 33 | 5 (installed 2018) | 100 | [5 empty] | UUG1103
United Utilities | WINDMILL LANE CSO 44012 | Windmill Lane CSO | 016983013 | TAM0172 | SO | SO on sewer network | SJ9115094820 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | DENTON BROOK VIA CLVR WCOURSE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 5.66 | 33 | 20.8 | 5 (installed 2018) | 99.98 | [5 empty] | UUG1104
United Utilities | ROSS LAVE LANE CSO | Ross Lave Lane CSO | 016983312 | TAM0175 | SO | SO on sewer network | SJ9159094450 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | UNNAMED TRIB OF DENTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 150.81 | 79 | 68 | 5 (installed 2018) | 99.92 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1105
United Utilities | OFF FOXHOLES ROAD CSO | Off Foxholes Road CSO | 016993392 | TAM0176 | SO | SO on sewer network | SJ9434094000 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | TRIB OF RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.9 | 6 | 9.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG1106
United Utilities | DENTON TRANSFER PUMPING STATION | Denton Transfer PS | 016993917 | TAM0177 | SO | Storm discharge at pumping station | SJ9227093380 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 458.93 | 100 | 33.3333 | 3 (installed 2020) | 99.99 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1107
United Utilities | DENTON TRANSFER PUMPING STATION | Denton Transfer PS | 016993917 | TAM0177 | ST | Storm discharge at pumping station | SJ9227093380 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 677.2 | 59 | 82.3333 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1108
United Utilities | HUYTON WASTEWATER TREATMENT WORKS | HUYTON WwTW | 016930121 | 16930121 | SO | Inlet SO at WwTW | SJ4473088840 | GB112069060680 | Netherley Brook | DITTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 723.13 | 92 | 98.4 | 5 (installed 2018) | 98.94 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1109
United Utilities | HUYTON WASTEWATER TREATMENT WORKS | HUYTON WwTW | 016930121 | 16930121 | ST | Storm tank at WwTW | SJ4473088840 | GB112069060680 | Netherley Brook | DITTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1063.99 | 75 | 41.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1110
United Utilities | HUYTON FARM PUMPING STATION | Huyton Farm PS | 016997049 | KNW0006 | SO | Storm discharge at pumping station | SJ4234092560 | GB112069060580 | Alt | UN-NAMED TRIB. OF RIVER ALT | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1111
United Utilities | LINK ROAD COMBINED SEWER OVERFLOW | LINK ROAD CSO | 01KNW0009 | KNW0009 | SO | SO on sewer network | SJ4580090090 | GB112069060710 | Prescot Brook (Logwood Mill Brook) | LOGWOOD MILL BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 5 | 11 | 9.25 | 4 (installed 2019) | 100 | [5 empty] | UUG1112
United Utilities | WHISTON PARK (ECCLESTON PK) CSO | Whiston Eccleston Park CSO | 016983003 | KNW0017 | SO | SO on sewer network | SJ4589089890 | GB112069060710 | Prescot Brook (Logwood Mill Brook) | LONGWOOD MILL BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 162.6 | 46 | 36.5 | 4 (installed 2019) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1113
United Utilities | MOLYNEUX DRIVE CSO 24009 | Molyneux Drive CSO | 016993826 | KNW0021 | SO | SO on sewer network | SJ4581090940 | GB112069060710 | Prescot Brook (Logwood Mill Brook) | PRESCOT BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 72.55 | 68 | 63.2 | 5 (installed 2018) | 99.82 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1114
United Utilities | KING GEORGE PRESCOT CSO | King George V Memorial Playing Field | 016930642 | KNW0024 | SO | SO on sewer network | SJ4613092260 | GB112069060710 | Prescot Brook (Logwood Mill Brook) | PRESCOT BROOK TRIB DITTON BRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 215.59 | 56 | 46 | 4 (installed 2019) | 66.63 | Telemetry or data archiving failure / issue | N/A - Ongoing investigation | Data collection - EDM non-representative location | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1115
United Utilities | HUTTON ROOF STW | HUTTON ROOF WwTW | 017370069 | 17370069 | SO | Inlet SO at WwTW | SD5705077900 | GB112073071080 | Lupton (Farleton) Beck | SEALFORD BECK | N/A | N/A | Not Applicable | Dec 2023 | 15.76 | 8 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1116
United Utilities | HURST GREEN WWTW | Hurst Green WwTW | 017160040 | 17160040 | ST | Storm tank at WwTW | SD6910037750 | GB112071065500 | Ribble - conf Calder to tidal | DEAN BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2659.24 | 219 | 207.75 | 4 (installed 2019) | 97.53 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1117
United Utilities | HUNSONBY CSO (171ME) | Hunsonby CSO | 017680354 | EDE0108 | SO | SO on sewer network | NY5807035440 | GB102076073810 | Robberby Water | ROBBERBY WATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 99.99 | [5 empty] | UUG1118
United Utilities | HULTON LANE ENDS STW | HULTON LANE ENDS WwTW | 016950037 | 16950037 | SO | Inlet SO at WwTW | SD7630004030 | GB112069061451 | Irwell (Croal to Irk) | UNITY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 526.74 | 80 | 69 | 3 (installed 2020) | 97.78 |  |  | Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1119
United Utilities | HORWICH WASTEWATER TREATMENT WORKS | HORWICH WwTW | 017050012 | 17050012 | SO | Inlet SO at WwTW | SD6264010763 | GB112070064850 | Douglas - Upper | PEARL BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 376.97 | 56 | 68.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1120
United Utilities | HORWICH WASTEWATER TREATMENT WORKS | HORWICH WwTW | 017050012 | 17050012 | ST | Storm tank at WwTW | SD6264010763 | GB112070064850 | Douglas - Upper | PEARL BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 381.64 | 47 | 58.8 | 5 (installed 2018) | 87.94 | Sensor failure / issue | Resolved - Feb | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1121
United Utilities | CHORLEY NEW RD TELFORD ST CSO 071JQ | CHORLEY NEW ROAD / TELFORD STREET CSO | 01BOL0133 | BOL0133 | SO | SO on sewer network | SD6440010670 | GB112070064850 | Douglas - Upper | MIDDLE BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.13 | 1 | 9.2 | 5 (installed 2018) | 91.49 | [5 empty] | UUG1122
United Utilities | WOODBARN FARM CSO 07059 | Wood Barn Farm CSO | 017091505 | BOL0141 | SO | SO on sewer network | SD6209010990 | GB112070064850 | Douglas - Upper | UNNAMED TRIB THE RIVER DOUGLAS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 141.75 | 62 | 75.2 | 5 (installed 2018) | 92.93 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1123
United Utilities | JCT OF MANCHESTER RD/STATION RD CSO | Junction of Manchester/Station Road CSO | 01BOL0142 | BOL0142 | SO | SO on sewer network | SD6240009950 | GB112069064540 | Croal Minor | UNNAMED TRIB OF MIDDLE BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 7 | 19 | 33.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1124
United Utilities | PARK HALL FARM CSO 071EY | PARK HALL FARM CSO | 01BOL0143 | BOL0143 | SO | SO on sewer network | SD6271009630 | GB112069064540 | Croal Minor | UNNAMED TRIB OF MIDDLE BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 156.33 | 81 | 73.8 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1125
United Utilities | MANCHESTER RD/HOPE ST | Manchester Road/Hope Street CSO | 016982615 | BOL0199 | SO | SO on sewer network | SD6229009720 | GB112069064540 | Croal Minor | RIVER CROAL | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1126
United Utilities | HORTON-IN-RIBBLESDALE STW | HORTON-IN-RIBBLESDALE WwTW | 017160039 | 17160039 | ST | Storm tank at WwTW | SD8071572125 | GB112071065640 | Ribble - Brants Ghyll to conf Stainforth Beck | RIVER RIBBLE | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2480.55 | 144 | 129.5 | 4 (installed 2019) | 100 |  |  | Performance - Partial / no capacity due to blockage or restriction (e.g. roots / grid) - maintenance issue | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1127
United Utilities | HORNBY STW | HORNBY WwTW | 017270017 | 17270017 | SO | Inlet SO at WwTW | SD5805068390 | GB112072065990 | Wenning - Lower | RIVER WENNING | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 10.63 | 29 | 46 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1128
United Utilities | HOLMES CHAPEL STW | HOLMES CHAPEL WwTW | 016810081 | 16810081 | ST | Storm tank at WwTW | SJ7515067590 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 874.34 | 64 | 78.25 | 4 (installed 2019) | 96.81 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1129
United Utilities | ALUM BRIDGE PUMPING STATION | Alum Bridge PS | 01CON0064 | CON0064 | SO | Storm discharge at pumping station | SJ7650066500 | GB112068055460 | Croco | RIVER CROCO | N/A | N/A | Not Applicable | Dec 2023 | 3.44 | 1 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1130
United Utilities | HOLME WWTW | HOLME WwTW | 017370138 | 17370138 | ST | Storm tank at WwTW | SD5179078540 | GB112073071050 | Holme Beck | HOLME BECK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 1 | 2 | 46.2857 | 7 (installed 2016) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1131
United Utilities | DUKE STREET | Duke Street CSO | 01LAK0044 | LAK0044 | SO | SO on sewer network | SD5171078500 | GB112073071050 | Holme Beck | HOLME BECK | N/A | N/A | Not Applicable | Dec 2023 | 511.93 | 90 |  | <1 yr (installed 2023) | 96.3964 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1132
United Utilities | HOLME STATION CSO 391HY LAK0046 | Holme Station CSO | 017370154 | LAK0046 | SO | SO on sewer network | SD5227077300 | GB112073071050 | Holme Beck | EWAN MILL BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 224.4 | 27 | 19.5 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1133
United Utilities | HILLHOUSE WWTW | HILLHOUSE WwTW | 016930111 | 16930111 | ST | Storm tank at WwTW | SD3501005590 | GB112069061442 | Alt DS Bull Bridge | HEY COP DRAIN, TRIB RIVER ALT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 677.18 | 79 | 70.4 | 5 (installed 2018) | 99.93 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1134
United Utilities | BRADFIELD AVENUE CSO 318FN | BRADFIELD AVENUE CSO | 01SEF0011 | SEF0011 | SO | SO on sewer network | SJ3718099520 | GB112069061441 | Alt US Bull Bridge | MOOR HEY BROOK TRIB RVR ALT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 3.5 | 4 | 5.6 | 5 (installed 2018) | 100 | [5 empty] | UUG1135
United Utilities | BRIDGE RD JCT COPY LANE | Dunning's Bridge Road, Junction Copy Lane CSO | 01SEF0010 | SEF0010 | SO | SO on sewer network | SJ3696099830 | GB112069061441 | Alt US Bull Bridge | MOOR HEY BROOK | N/A | N/A | Not Applicable | Dec 2023 | 7.63 | 10 |  | <1 yr (installed 2023) | 81.0526 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1136
United Utilities | REAR 23 LIVERPOOL ROAD NORTH CSO | Rear 23 Liverpool Road North CSO | 016997082 | SEF0015 | SO | SO on sewer network | SD3685002290 | GB112069061441 | Alt US Bull Bridge | MAGHULL BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1137
United Utilities | DOOLEY DRIVE CSO/ | Dooley Drive Combined Sewer Overflow (381N6) (SEF0065) ( Emergency Overflow for 38006 – Copy Lane Pumping Station | 016997071 | SEF0065 | SO | SO on sewer network | SJ3697099830 | GB112069061441 | Alt US Bull Bridge | MOOR HEY BRK TRIB OF R. ALT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 2.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1138
United Utilities | THORNTON PUMPING STATION THRTN | Thornton PS | 016930115 | SEF0115 | SO | Storm discharge at pumping station | SD3403002860 | GB112068060270 | Alt DS Bull Bridge | HUNTS BROOK | N/A | Formby | Not Applicable | Commissioned in 2017 - full year data expected | 105.62 | 21 | 98.3333 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1139
United Utilities | WATERLOO ROAD CSO (202ZW) | Waterloo Road Sewer | 016820393 | HAL0031 | SO | SO on sewer network | SJ5104083300 | 169 |  | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1.4 | 10 | 7.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG1140
United Utilities | HIGH BENTHAM WWTW (HGHBE) | HIGH BENTHAM WwTW | 017260004 | 17260004 | SO | Inlet SO at WwTW | SD6589069140 | GB112072065990 | Wenning - Lower | RIVER WENNING | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 411.75 | 115 | 107.75 | 4 (installed 2019) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1141
United Utilities | HIGH BENTHAM WWTW (HGHBE) | HIGH BENTHAM WwTW | 017260004 | 17260004 | ST | Storm tank at WwTW | SD6589069140 | GB112072065990 | Wenning - Lower | RIVER WENNING | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1173.24 | 97 | 103.75 | 4 (installed 2019) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1142
United Utilities | HESKETH BANK WWTW HSKBK | HESKETH BANK WwTW | 017030023 | 17030023 | ST | Storm tank at WwTW | SD4562023980 | GB531207112400 | RIBBLE | DOUGLAS ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 45.67 | 10 | 14.8333 | 6 (installed 2017) | 99.95 | [5 empty] | UUG1143
United Utilities | TRENTHAM P.S | Trentham Street PS | 016820392 | HAL0029 | SO | Storm discharge at pumping station | SJ5070083441 | 169 |  | RIVER MERSEY | N/A | N/A | Not Applicable | Dec 2023 | 7.82 | 48 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1144
United Utilities | HELSBY WWTW | HELSBY WwTW | 016810187 | 16810187 | SO | Inlet SO at WwTW | SJ4815275072 | GB112068060330 | Peckmill Brook, Hoolpool Gutter at Ince Marshes. | HORNSMILL BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 70.83 | 17 | 12.2 | 5 (installed 2018) | 99.54 | [5 empty] | UUG1145
United Utilities | HELSBY WWTW | HELSBY WwTW | 016810187 | 16810187 | ST | Storm tank at WwTW | SJ4815275072 | GB112068060330 | Peckmill Brook, Hoolpool Gutter at Ince Marshes. | HORNSMILL BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 21.75 | 3 | 10 | 5 (installed 2018) | 99.83 | [5 empty] | UUG1146
United Utilities | HAPSFORD SPS | Hapsford PS | 016810286 | CHE0015 | SO | Storm discharge at pumping station | SJ4713074550 | GB112068060330 | Peckmill Brook, Hoolpool Gutter at Ince Marshes. | HORNSMILL BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 23.68 | 14 | 18.3333 | 3 (installed 2020) | 99.96 | [5 empty] | UUG1147
United Utilities | ELTON PS | Elton PS | 01CHE0025 | CHE0025 | SO | Storm discharge at pumping station | SJ4646075690 | GB112068060330 | Peckmill Brook, Hoolpool Gutter at Ince Marshes. | WEST CENTRAL DRAIN, MERSEY EST | N/A | N/A | Not Applicable | Dec 2023 | 6.23 | 3 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1148
United Utilities | WATERSIDE DRIVE CSO 472H4 | Waterside Drive CSO | 01VRY0057 | VRY0057 | SO | SO on sewer network | SJ5253079050 | GB112068060500 | Weaver (Dane to Frodsham) | RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 70.5 | 34 | 25.6 | 5 (installed 2018) | 99.99 | [5 empty] | UUG1149
United Utilities | HIGH STREET/MOORS LANE CSO | High Street/Moors Lane CSO | 01VRY0059 | VRY0059 | SO | SO on sewer network | SJ5140078190 | GB112068060500 | Weaver (Dane to Frodsham) | MAIN DRAIN (TRIB RIVER WEAVER) | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 19.23 | 32 | 105.5714 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1150
United Utilities | NEWTOWN PUMPING STATION | Newtown PS | 016983017 | VRY0132 | SO | Storm discharge at pumping station | SJ5258079030 | GB112068060500 | Weaver (Dane to Frodsham) | RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 207.99 | 46 | 16.6 | 5 (installed 2018) | 99.96 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1151
United Utilities | HATLEY LANE COMBINED SEWER OVERFLOW | Hatley Lane | 016881726 | VRY0139 | SO | SO on sewer network | SJ5070077310 | GB112068060500 | Weaver (Dane to Frodsham) | FRODSHAM MARSH DITCH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 6.9 | 14 | 15.25 | 4 (installed 2019) | 100 | [5 empty] | UUG1152
United Utilities | BRIDGE LANE QUAYSIDE CSO | Bridge Lane | 016881727 | VRY0140 | SO | SO on sewer network | SJ5296078430 | GB112068060500 | Weaver (Dane to Frodsham) | RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2.27 | 9 | 9.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1153
United Utilities | HELLIFIELD STW | HELLIFIELD WwTW | 017160036 | 17160036 | SO | Inlet SO at WwTW | SD8475856288 | GB112071065613 | Ribble (Long Preston to Stock Beck) | HELLIFIELD (PAN) BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 119.7 | 3 (installed 2020) | 100 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1154
United Utilities | HELLIFIELD STW | HELLIFIELD WwTW | 017160036 | 17160036 | ST | Storm tank at WwTW | SD8475856288 | GB112071065613 | Ribble (Long Preston to Stock Beck) | HELLIFIELD (PAN) BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 935.48 | 165 | 55 | 3 (installed 2020) | 100 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1155
United Utilities | HEADS NOOK WWTW | HEADS NOOK WwTW | 017670062 | 17670062 | SO | Inlet SO at WwTW | NY4903055070 | GB102076073870 | Cairn Beck | CAIRN BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 83.54 | 51 | 68.25 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1156
United Utilities | HEADS NOOK PUMPING STATION | Heads Nook Pumping Station (10507) (CAR0080) | 017680325 | CAR0080 | SO | Storm discharge at pumping station | NY4961055290 | GB102076073900 | Trout Beck (Cairn Beck) | TRIB TROUT BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 5 (installed 2018) | 100 | [5 empty] | UUG1157
United Utilities | HAZEL GROVE STW | Hazel Grove WwTW | 016940175 | 16940175 | ST | Storm tank at WwTW | SJ9312089440 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 952.74 | 81 | 72.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1158
United Utilities | COPPICESIDE PS DISLEY | Coppiceside PS | 016940142 | MAC0159 | SO | Storm discharge at pumping station | SJ9585084620 | GB112069060920 | Micker (Norbury) Brook | BOLLINHURST BROOK | N/A | N/A | Not Applicable | Dec 2023 | 852.14 | 63 |  | <1 yr (installed 2023) | 100 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1159
United Utilities | BUXTON RD ANDREW LN CSO 435GX | Buxton Road/Andrew Lane CSO | 01STK0093 | STK0093 | SO | SO on sewer network | SJ9556085430 | GB112069060950 | Poise Brook | UNNAMED BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 12.07 | 32 | 162.8 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1160
United Utilities | HAZELWOOD ROAD CSO 435GY | Hazelwood Road combined sewer overflow (435GY) (STK0094) | 016982761 | STK0094 | SO | SO on sewer network | SJ9269087210 | GB112069060950 | Poise Brook | POISE BROOK TRIB RVR GOYT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 26.83 | 53 | 56.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1161
United Utilities | MARPLE ROAD COMBINED SEWER OVERFLOW | Marple Road CSO | 016982662 | STK0096 | SO | SO on sewer network | SJ9266088870 | GB112069060950 | Poise Brook | POISE BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 24.7 | 30 | 30 | 6 (installed 2017) | 100 | [5 empty] | UUG1162
United Utilities | OPP 255 BUXTON ROAD | Opposite 255 Buxton Road CSO | 016982663 | STK0097 | SO | SO on sewer network | SJ9355085860 | GB112069060950 | Poise Brook | HAZEL GROVE BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1163
United Utilities | TORKINGTON ROAD CSO | Torkington Road CSO | 016982664 | STK0098 | SO | SO on sewer network | SJ9338087070 | GB112069060950 | Poise Brook | TRIB OF OCHERLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.03 | 1 | 0.66667 | 3 (installed 2020) | 100 | [5 empty] | UUG1164
United Utilities | 36 HIBBERT LANE CSO 431Y7 | 36 Hibbert Lane CSO | 01STK0099 | STK0099 | SO | SO on sewer network | SJ9527088420 | GB112069061000 | Goyt (Etherow to Mersey) | MARPLE BRK TRIB TORKINGTON BR | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.07 | 1 | 2.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1165
United Utilities | BONGS VALLEY PUMPING STATION | Bongs Valley PS | 016983106 | STK0142 | SO | Storm discharge at pumping station | SJ9321089140 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 216.43 | 60 | 90.75 | 4 (installed 2019) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1166
United Utilities | BONGS ROAD COMBINED SEWER OVERFLOW | Bongs Road CSO | 016892302 | STK0147 | SO | SO on sewer network | SJ9329689008 | GB112069061000 | Goyt (Etherow to Mersey) | RIVER GOYT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 41.75 | 31 | 38.5 | 4 (installed 2019) | 84.69 | Capital / maintenance works affect EDM operation | Resolved - Aug |  |  | Other investigation - non-WINEP/Green Recovery | UUG1167
United Utilities | 19 WOOD LANE CSO | 19 Wood Lane (Marple) CSO | 016892515 | STK0148 | SO | SO on sewer network | SJ9476088370 | GB112069061000 | Goyt (Etherow to Mersey) | TRIB TORKINGTON BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1.07 | 2 | 1.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG1168
United Utilities | STOCKPORT ROAD/HILL TOP DRIVE CSO | Stockport Road CSO | NPSWQD010103 | STK0149 | SO | SO on sewer network | SJ9429988849 | GB112069061000 | Goyt (Etherow to Mersey) | MARPLE BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 100 | [5 empty] | UUG1169
United Utilities | CORFE CRESCENT CSO | Outside No.X Corfe Crescent CSO | NPSWQD010100 | STK0150 | SO | SO on sewer network | SJ9149086250 | GB112069060920 | Micker (Norbury) Brook | NORBURY BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0.33333 | 3 (installed 2020) | 100 | [5 empty] | UUG1170
United Utilities | 56 Cross Lane combined sewer overflow (STK0152) | 56 Cross Lane combined sewer overflow (STK0152) | EPR/JB3891RX | STK0152 | SO | SO on sewer network | SJ9520088492 | GB112069061000 | Goyt (Etherow to Mersey) | Un-named tributary of Marple Brook | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1171
United Utilities | HAYTON STW | HAYTON WwTW | 017570084 | 17570084 | ST | Storm tank at WwTW | NY1076041830 | GB112075073660 | Crookhurst Beck | PATTEN BECK | N/A | Allonby | Not Applicable | Commissioned in 2016 - full year data expected | 1634.75 | 133 | 130 | 7 (installed 2016) | 99.52 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1172
United Utilities | GRANGE FARM COMBINED SEWER OVERFLOW | Grange Farm CSO | 017580318 | ALL0020 | SO | SO on sewer network | NY1096041640 | GB112075073660 | Crookhurst Beck | TRIBUTARY OF PATTEN BECK | N/A | Allonby | Not Applicable | Commissioned in 2016 - full year data expected | 10 | 16 | 23.8571 | 7 (installed 2016) | 99.94 | [5 empty] | UUG1173
United Utilities | HAYFIELD WASTEWATER TREATMENT WORKS | HAYFIELD WwTW | 016940174 | 16940174 | ST | Storm tank at WwTW | SK0266087140 | GB112069060970 | Sett | RIVER SETT | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 2178.24 | 126 | 115.1667 | 6 (installed 2017) | 95.97 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Resolved - Oct | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1174
United Utilities | SWALLOW HOUSE LANE CSO 212UB | Swallow House Lane Combined Sewer Overflow (Site ID 212UB) (PEA0057) | 01PEA0057 | PEA0057 | SO | SO on sewer network | SK0308087350 | GB112069060970 | Sett | HOLLINGWORTH CLOUGH | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 93.37 | 58 | 38.3333 | 6 (installed 2017) | 99.75 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1175
United Utilities | HAWKSHEAD PUMPING STATION | Hawkshead Pumping Station (Site ID HWKSH) (LAK0107) | 017380284 | LAK0107 | SO | Storm discharge at pumping station | SD3552197931 | GB112073071400 | Cunsey Beck/Black Beck | BLACK BECK | N/A | Windermere, Rayrigg Meadow | Not Applicable | Commissioned in 2017 - full year data expected | 2407.19 | 154 | 153.1667 | 6 (installed 2017) | 96.98 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | U_INV driver - Stage 4: No cost beneficial solution | UUG1176
United Utilities | LOW WOOD BRIDGE PUMPING STATION | Low Wood Bridge Pumping Station (Site ID LOWWO) (LAK0054) | 017380340 | LAK0054 | SO | Storm discharge at pumping station | SD3453083680 | GB112073071420 | Leven | RIVER LEVEN | N/A | Morecambe | Not Applicable | Commissioned in 2016 - full year data expected | 78.4 | 33 | 38.2857 | 7 (installed 2016) | 100 | [5 empty] | UUG1177
United Utilities | HALTON WEST PUMPING STATION HLTWE | Halton West SPS | 017280287 | LAN0097 | SO | Storm discharge at pumping station | SD4998064660 | GB112072065980 | Lune - conf Wenning to tidal | RIVER LUNE | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 62.26 | 51 | 40 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity |  | UUG1178
United Utilities | HALTON EAST STW | HALTON EAST WwTW | 017270002 | 17270002 | ST | Storm tank at WwTW | SD5053064611 | GB112072065980 | Lune - conf Wenning to tidal | RIVER LUNE | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 663.22 | 63 | 56.4286 | 7 (installed 2016) | 100 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Resolved - Nov | Other investigation - non-WINEP/Green Recovery | UUG1179
United Utilities | HALTON EAST SEWAGE PUMPING STATION | Halton East sewage pumping station (Site ID HALTN) (LAN0060 | 01LAN0060 | LAN0060 | SO | Storm discharge at pumping station | SD5030064700 | GB112072065980 | Lune - conf Wenning to tidal | RIVER LUNE | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 148.82 | 88 | 69.1429 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1180
United Utilities | GRINDLETON WWTW | GRINDLETON WwTW | 017160035 | 17160035 | ST | Storm tank at WwTW | SD7569044770 | GB112071065612 | Ribble DS Stock Beck | RIVER RIBBLE/WEST CLOUGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1625.67 | 143 | 136 | 4 (installed 2019) | 99.84 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1181
United Utilities | REAR OF NO.4 RIBBLE AVENUE CSO | REAR OF No4 RIBBLE AVENUE CSO | 01RIB0007 | RIB0007 | SO | SO on sewer network | SD7590045150 | GB112071065612 | Ribble DS Stock Beck | CULVERTED GRINDLETON BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 75.13 | 43 | 39.6667 | 3 (installed 2020) | 99.99 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1182
United Utilities | GREYSTOKE WWTW | GREYSTOKE WwTW | 017670101 | 17670101 | SO | Inlet SO at WwTW | NY4459031190 | GB102076073992 | Petteril u/s M6 | RIVER PETTERIL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.22 | 1 | 9.75 | 4 (installed 2019) | 100 | [5 empty] | UUG1183
United Utilities | GREYSTOKE PS | Greystoke Wastewater Process PS | 017670163 | EDE0059 | SO | Storm discharge at pumping station | NY4356030770 | GB102076073992 | Petteril u/s M6 | RIVER NORTH PETTERIL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2514.07 | 146 | 141.25 | 4 (installed 2019) | 100 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1184
United Utilities | GREYSOUTHEN WWTW | GREYSOUTHEN WwTW | 017570043 | 17570043 | SO | Inlet SO at WwTW | NY0716030400 | GB112075070520 | Derwent - conf Cocker to tidal | TRIB RIVER DERWENT | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 508.82 | 98 | 102 | 3 (installed 2020) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1185
United Utilities | THE CSO AT MAIN STREET | The CSO at Main Street | 017580276 | ALL0129 | SO | SO on sewer network | NY0711628810 | GB112075070540 | Marron | TOWNSEND BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.07 | 3 | 3 | 5 (installed 2018) | 100 | [5 empty] | UUG1186
United Utilities | SANDLE BRIDGE WW NETWORK PS | Sandle Bridge Wastewater Network PS | 016892278 | MAC0098 | SO | Storm discharge at pumping station | SJ8072076830 | GB112069061340 | Birkin Brook - Source to Mobberley Brook | PEDLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 13.73 | 5 | 22.5 | 4 (installed 2019) | 77.74 | Comms failure / issue | Resolved - Sep |  |  |  | UUG1187
United Utilities | OLLERTON SEWAGE PUMPING STATION | Ollerton PS | 016910012 | MAC0147 | SO | Storm discharge at pumping station | SJ7806076861 | GB112069061340 | Birkin Brook - Source to Mobberley Brook | TRIB MARTHALL BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 363.95 | 65 | 40.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1188
United Utilities | GREAT SALKELD WWTW GRSAL | GREAT SALKELD WwTW | 017670061 | 17670061 | SO | Inlet SO at WwTW | NY5569036430 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 229.93 | 70 | 95.8333 | 6 (installed 2017) | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP or Green Recovery | UUG1189
United Utilities | GREAT ORTON WWTW (GRORT) | GREAT ORTON WwTW | 017670128 | 17670128 | ST | Storm tank at WwTW | NY3332054490 | GB102076073950 | Powburgh Beck | ROUGHTON BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 3114.6 | 176 | 154.5 | 4 (installed 2019) | 99.99 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1190
United Utilities | GREAT BROUGHTON WWTW | GREAT BROUGHTON WwTW | 017570041 | 17570041 | SO | Inlet SO at WwTW | NY0706030500 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 334.05 | 97 | 106.8 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1191
United Utilities | GREAT BROUGHTON WWTW | GREAT BROUGHTON WwTW | 017570041 | 17570041 | ST | Storm tank at WwTW | NY0706030500 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1690.93 | 184 | 301.6 | 5 (installed 2018) | 100 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Stage 1c: Confirmed "hydraulic issue" | UUG1192
United Utilities | GREAT ASBY WWTW | GREAT ASBY WwTW | 017680364 | 17680364 | SO | Inlet SO at WwTW | NY6859013710 | GB102076070630 | Hoff Beck (upper) | ASBY BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 535.69 | 91 | 142.5 | 4 (installed 2019) | 99.93 |  |  | Performance - Infiltration | Resolved - Nov | Other investigation - non-WINEP/Green Recovery | UUG1193
United Utilities | GRASMERE WWTW | Grasmere Waste Water Treatment Works | 017370027 | 17370027 | SO | Inlet SO at WwTW | NY3392006840 | GB112073071140 | Rothay | GRASMERE LAKE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2532 | 105 | 83.6 | 5 (installed 2018) | 98.77 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1194
United Utilities | THE BROW CSO 202UP | The Brow CSO | 016892107 | HAL0055 | SO | SO on sewer network | SJ5315083440 | 169 |  | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 4.93 | 16 | 13.6667 | 6 (installed 2017) | 100 | [5 empty] | UUG1195
United Utilities | DOWNS ROAD COMBINED SEWER OVERFLOW | Downs Road CSO | 016892108 | HAL0056 | SO | SO on sewer network | SJ5163082730 | 169 |  | BRIDGEWATER CANAL VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.93 | 8 | 6.25 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1196
United Utilities | PROMENADE COMBINED SEWER OVERFLOW | Promenade CSO | 017370196 | LAK0072 | SO | SO on sewer network | SD4067077560 | GB531207312000 | KENT | THE KENT CHANNEL MORECAMBE BAY | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.37 | 4 | 29.2 | 5 (installed 2018) | 54.9 | Comms failure / issue | Resolved - January after reporting year |  |  |  | UUG1197
United Utilities | PENN LANE WESTON POINT PR CSO 202LE | Penn Lane (Weston Point, Point R) combined sewer overflow (202LE) (HAL0060) | 01HAL0060 | HAL0060 | SO | SO on sewer network | SJ4977082451 | 169 |  | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 89.27 | 76 | 73.8 | 5 (installed 2018) | 99.99 |  |  | Data collection - EDM non-representative location | Resolved - Oct | Stage 1c: Confirmed "hydraulic issue" | UUG1198
United Utilities | GRANGE PUMPING STATION | Grange PS | 017380194 | LAK0074 | SO | Storm discharge at pumping station | SD4125078160 | GB531207312000 | KENT | KENT ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 147.08 | 32 | 46.1667 | 6 (installed 2017) | 99.92 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1199
United Utilities | CARK TANK NO.1 PUMPINT STATION | Cark PS | 01LAK0076 | LAK0076 | SO | Storm discharge at pumping station | SD3578076410 | GB112073071270 | Eea | RIVER EEA | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 73.4 | 5 (installed 2018) | 100 |  |  | Performance - Infiltration | Resolved - Jan | Stage 1b: Confirmed "asset maintenance" issue | UUG1200
United Utilities | EXPRESSWAY 8 RUNCORN | Expressway 8, Runcorn (Weston Point, Point R) CSO | 01HAL0061 | HAL0061 | SO | SO on sewer network | SJ4977082450 | 169 |  | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 143.23 | 82 | 54.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1201
United Utilities | CARTMEL IN CARK PUMPING STATION | Cartmel In Cark Pumping Station (Site ID CARTC) (LAK0099) | 017380400 | LAK0099 | SO | Storm discharge at pumping station | SD3651076350 | GB112073071270 | Eea | RIVER EEA | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 6471.57 | 281 | 327 | 5 (installed 2018) | 99.52 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1202
United Utilities | HALTON BROW CSO 203EF | Halton Brow CSO | 01HAL0062 | HAL0062 | SO | SO on sewer network | SJ5315083431 | 169 |  | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 84 | 89 | 99.4 | 5 (installed 2018) | 99.73 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1203
United Utilities | GRANGE BRIDGE PS GNGBO ALL0062 | Grange Bridge (200mtrs downstream) | 017570113 | ALL0062 | SO | Storm discharge at pumping station | NY2550017600 | GB112075070410 | Derwent - Stonethwaite Beck to conf Greta | RIVER DERWENT | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 607.2 | 64 | 62 | 7 (installed 2016) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1204
United Utilities | GOSFORTH WWTW | GOSFORTH WwTW | 017470040 | 17470040 | ST | Storm tank at WwTW | NY0782002750 | GB112074070090 | Bleng | HARE BECK | N/A | Seascale | Not Applicable | Commissioned in 2016 - full year data expected | 2.34 | 4 | 38.5714 | 7 (installed 2016) | 100 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG1205
United Utilities | MEADOWFIELD GOSFORTH CSO | Meadowfield Gosforth Combined Sewer Overflow (Site ID 02631) (COP0030) | 01COP0030 | COP0030 | SO | SO on sewer network | NY0685003370 | GB112074070090 | Bleng | ESK | N/A | Seascale | Not Applicable | Commissioned in 2016 - full year data expected | 12.76 | 8 | 14 | 7 (installed 2016) | 99.85 | [5 empty] | UUG1206
United Utilities | GLOSSOP STW (SPS) | GLOSSOP WwTW | 016940172 | 16940172 | ST | Storm tank at WwTW | SK0058094910 | GB112069061050 | Etherow (Glossop Brook to Goyt) | TRIB RIVER ETHEROW | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 2530.16 | 172 | 162.3333 | 3 (installed 2020) | 99.96 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Stage 1c: Confirmed "hydraulic issue" | UUG1207
United Utilities | CORNMILL BRIDGE CSO | Cornmill Bridge CSO | 016993523 | PEA0027 | SO | SO on sewer network | SK0397094170 | GB112069060730 | Glossop (Shelf) Brook (Source to Long Clough Brook) | SHELF BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 241.94 | 46 | 75.3333 | 3 (installed 2020) | 99.92 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1208
United Utilities | HIGH ST WEST CSO (21120) | High Street West CSO | 016892339 | PEA0028 | SO | SO on sewer network | SK0225094190 | GB112069060720 | Glossop Brook (Long Clough Brook to Etherow) | GLOSSOP BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 285.6 | 48 | 31.6667 | 3 (installed 2020) | 99.99 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1209
United Utilities | PRIMROSE LANE CSO | Primrose Lane CSO | 016892340 | PEA0029 | SO | SO on sewer network | SK0232094110 | GB112069060700 | Long Clough Brook | LONG CLOUGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 113.72 | 70 | 63 | 3 (installed 2020) | 95.1 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1210
United Utilities | ST MARYS RD COMBINED SEWER OVERFLOW | CSO opposite No. XX St Mary's Road | 016993589 | PEA0033 | SO | SO on sewer network | SK0311093940 | GB112069060730 | Glossop (Shelf) Brook (Source to Long Clough Brook) | GLOSSOP BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.63 | 4 | 9.25 | 4 (installed 2019) | 100 | [5 empty] | UUG1211
United Utilities | VICTORIA ST CSO 212WG | Victoria Street CSO | 01PEA0034 | PEA0034 | SO | SO on sewer network | SK0346093940 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.17 | 1 | 1.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG1212
United Utilities | SPRING TAVERN CSO 218NH | Spring Tavern CSO | 016982492 | PEA0036 | SO | SO on sewer network | SK0092095820 | GB112069060780 | Etherow (Woodhead Res. to Glossop Bk.) | RIVER ETHEROW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 659.63 | 111 | 99.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1213
United Utilities | SHAW LANE CSO 212Q4 | Shaw Lane CSO | 016892342 | PEA0037 | SO | SO on sewer network | SK0143094980 | GB112069060720 | Glossop Brook (Long Clough Brook to Etherow) | GLOSSOP BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.63 | 2 | 5 | 5 (installed 2018) | 96.56 | [5 empty] | UUG1214
United Utilities | WATERSIDE MILL CSO 212ZY | Waterside Mill CSO | 01PEA0039 | PEA0039 | SO | SO on sewer network | SK0193096510 | GB112069060780 | Etherow (Woodhead Res. to Glossop Bk.) | RIVER ETHEROW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 4.4 | 5 (installed 2018) | 99.99 | [5 empty] | UUG1215
United Utilities | BANKBOTTOM COMBINED SEWER OVERFLOW | Bankbottom CSO | 016892347 | PEA0040 | SO | SO on sewer network | SK0218096550 | GB112069060780 | Etherow (Woodhead Res. to Glossop Bk.) | TRIBUTARY OF RIVER ETHEROW | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.23 | 2 | 4.75 | 4 (installed 2019) | 100 | [5 empty] | UUG1216
United Utilities | High Street West CSO (AKA Dinting Lane CSO) | High Street West CSO (AKA Dinting Lane CSO) | 16892343 | PEA0030 | SO | SO on sewer network | SK0219094230 | GB112069060720 | Glossop Brook (Long Clough Brook to Etherow) | Glossop Brook | N/A | N/A | Not Applicable | Dec 2023 | 527.3 | 99 |  | <1 yr (installed 2023) | 97.3094 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1217
United Utilities | WOOLLEY BRIDGE ROAD CSO 43133 | Woolley Bridge Road CSO | 016993681 | PEA0069 | SO | SO on sewer network | SK0124096020 | GB112069060780 | Etherow (Woodhead Res. to Glossop Bk.) | RIVER ETHEROW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 156.99 | 65 | 61.8 | 5 (installed 2018) | 94.72 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1218
United Utilities | CHISWORTH MARPLE ROAD WWNPS | Chisworth (Marple Rd) WasteWater Network PS | 016982818 | PEA0071 | SO | Storm discharge at pumping station | SK0003092290 | GB112069061050 | Etherow (Glossop Brook to Goyt) | CHISWORTH BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 675.61 | 124 | 91.25 | 4 (installed 2019) | 99.43 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1219
United Utilities | PETER STREET CSO 212LL | Peter Street Combined Sewer Overflow (212LL) (PEA0082) | 016982638 | PEA0082 | SO | SO on sewer network | SK0207096970 | GB112069060780 | Etherow (Woodhead Res. to Glossop Bk.) | RIVER ETHEROW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 4 | 5 (installed 2018) | 99.72 | [5 empty] | UUG1220
United Utilities | NEWSHAW LANE CSO | Newshaw Lane CSO | 016982639 | PEA0083 | SO | SO on sewer network | SK0162095230 | GB112069060720 | Glossop Brook (Long Clough Brook to Etherow) | TRIB GLOSSOP BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 9.2 | 13 | 28.75 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1221
United Utilities | NORTH ROAD CSO (212IL) | North Road CSO | 016982640 | PEA0084 | SO | SO on sewer network | SK0309094530 | GB112075073660 | Crookhurst Beck | UNNAMED TRIB OF SANDWITH BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 133.83 | 43 | 61 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1222
United Utilities | CHARLESWORTH PUMPING STATION | Charlesworth PS | 016892056 | PEA0091 | SO | Storm discharge at pumping station | SJ9975093350 | GB112069061050 | Etherow (Glossop Brook to Goyt) | RIVER ETHEROW | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 82.75 | 15 | 19.5 | 4 (installed 2019) | 99.98 | [5 empty] | UUG1223
United Utilities | MELANDRA ROAD PS | Melandra Road PS | 016982612 | PEA0081 | SO | Storm discharge at pumping station | SK0101095240 | GB112069060720 | Glossop Brook (Long Clough Brook to Etherow) | GLOSSOP BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 440.97 | 83 | 27.6667 | 3 (installed 2020) | 96.5 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1224
United Utilities | WHOOLLEY LANE CSO 44024 | Woolley Lane Combined Sewer Overflow (44024) (TAM0142) | 016993525 | TAM0142 | SO | SO on sewer network | SK0070095180 | GB112069061050 | Etherow (Glossop Brook to Goyt) | RIVER ETHEROW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 389.76 | 109 | 108.2 | 5 (installed 2018) | 94.5 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1225
United Utilities | GLENRIDDING WWTW GLNRI | GLENRIDDING WwTW | 017680367 | 17680367 | SO | Inlet SO at WwTW | NY3845016830 | GB102076070740 | Glenridding Beck | GLENRIDDING BECK | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 51.17 | 36 | 66.4286 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1226
United Utilities | GLAZEBURY STW | GLAZEBURY WwTW | 016920350 | 16920350 | ST | Storm tank at WwTW | SJ6768095920 | GB112069061420 | Glaze | RIVER GLAZE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 973.87 | 97 | 140.6667 | 3 (installed 2020) | 99.24 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1227
United Utilities | GLAZEBURY SPS | Ravens Bridge Sewage PS | 016920504 | WAR0024 | SO | Storm discharge at pumping station | SJ6756096090 | GB112069061420 | Glaze | RIVER GLAZE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 308.69 | 67 | 60 | 3 (installed 2020) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1228
United Utilities | WARRINGTON RD/WITHINGTON | Warrington Road/Withington Avenue | 01WAR0109 | WAR0109 | SO | SO on sewer network | SJ6608095240 | GB112069061420 | Glaze | Glaze | N/A | N/A | Not Applicable | Dec 2023 | 78.97 | 51 |  | <1 yr (installed 2023) | 99.3 | [5 empty] | UUG1229
United Utilities | HEY SHOOT LINE CSO | Hey Shoot Lane CSO | 016982504 | WAR0112 | SO | SO on sewer network | SJ6760095960 | GB112069061420 | Glaze | RIVER GLAZE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 99.44 | [5 empty] | UUG1230
United Utilities | MOSS LANE COMBINED SEWER OVERFLOW | Moss Lane CSO | EPRRB3090NV | WAR0124 | SO | SO on sewer network | SJ6750296050 | GB112069061420 | Glaze | GLAZE BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 56.52 | 16 | 21.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG1231
United Utilities | ROBIN HOOD PS | Robin Hood PS | 016993569 | WIG0142 | SO | Storm discharge at pumping station | SJ6468098300 | GB112069064520 | Hey/Borsdane Brook | Hey Brook | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 42.86 | 65 | 58 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1232
United Utilities | ROBIN HOOD PS | Robin Hood PS | 016993569 | WIG0142 | SO | Storm discharge at pumping station | SJ6468098300 | GB112069064520 | Hey/Borsdane Brook | Landside Brook via surface water sewer | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 43.47 | 12 | 18.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG1233
United Utilities | PENNINGTON MILL BRIDGE CSO | Pennington Mill bridge CSO | 01WIG0143 | WIG0143 | SO | SO on sewer network | SJ6541099210 | GB112069060760 | Pennington Brook (Glaze) | Pennington Brook (Glaze) | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 6.2 | 12 | 9.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1234
United Utilities | WINDSOR GROVE | Windsor Grove CSO | 01HAL0126 | HAL0126 | SO | SO on sewer network | SJ5188081850 | 169 |  | WILLOW BROOK | N/A | N/A | Not Applicable | Commissioned pre-2016 - full year data expected | 2085.33 | 173 | 21.6 | 8 (installed 2015) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1235
United Utilities | GLASSONBY VILLAGE WWTW | GLASSONBY VILLAGE WwTW | 017680299 | 17680299 | SO | Inlet SO at WwTW | NY5774439384 | GB102076073820 | Glassonby Beck | GLASSONBY BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1825.77 | 192 | 48 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1236
United Utilities | RUNCORN TOWN HALL CSO | Runcorn Town Hall CSO | 016881893 | HAL0133 | SO | SO on sewer network | SJ5177082100 | 169 |  | WILLOW BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 3.4 | 4 | 3 | 3 (installed 2020) | 100 | [5 empty] | UUG1237
United Utilities | LABURNUM GROVE | Laburnham Grove | 01HAL0127 | HAL0127 | SO | SO on sewer network | SJ5176082090 | 169 |  | Willow Brook | N/A | N/A | Not Applicable | Commissioned pre-2016 - full year data expected | 3614.57 | 206 | 25.8 | 8 (installed 2015) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1238
United Utilities | SILLOTH WASTEWATER TREATMENT WORKS | SILLOTH WwTW | 017570006 | 17570006 | SO | Inlet SO at WwTW | NY1087054120 | 90 |  | SOLWAY FIRTH AT SILLOTH BAY | 118 Sillloth | Silloth | Not Applicable | Commissioned in 2016 - full year data expected | 145.74 | 26 | 87.4286 | 7 (installed 2016) | 99.93 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1239
United Utilities | GREEN ROW SILLOTH | Greenrow (Silloth) PS | 017580260 | ALL0109 | SO | Storm discharge at pumping station | NY1124052680 | 90 |  | TRIB GREAT GUTTER | N/A | Silloth | Not Applicable | Commissioned in 2017 - full year data expected | 2.21 | 2 | 4 | 6 (installed 2017) | 100 | [5 empty] | UUG1240
United Utilities | DRUMBURGH PUMPING STATION DRMBU | Drumburgh PS | 017680458 | ALL0137 | SO | Storm discharge at pumping station | NY2674060070 | GB530207614700 | SOLWAY | TIDAL TRIB OF THE SOLWAY FIRTH | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 20.73 | 21 | 10.5 | 6 (installed 2017) | 100 | [5 empty] | UUG1241
United Utilities | GISBURN WWTW GISBN | GISBURN WwTW | 017160034 | 17160034 | SO | Inlet SO at WwTW | SD8190049520 | GB112071065612 | Ribble DS Stock Beck | RIVER RIBBLE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1017.03 | 116 | 143 | 5 (installed 2018) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1242
United Utilities | GISBURN WWTW GISBN | GISBURN WwTW | 017160034 | 17160034 | ST | Storm tank at WwTW | SD8190049520 | GB112071065612 | Ribble DS Stock Beck | RIVER RIBBLE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 488.75 | 40 | 52.2 | 5 (installed 2018) | 98.35 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1243
United Utilities | STIRK HOUSE HOTEL WWPS | Stirk House Hotel PS | 017160134 | RIB0029 | SO | Storm discharge at pumping station | SD8154048370 | GB112071065612 | Ribble DS Stock Beck | WHEATLEY BECK, TRIB R. RIBBLE | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1175.84 | 76 | 47.5 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1244
United Utilities | GILSLAND WWTW | GILSLAND WwTW | 017670091 | 17670091 | SO | Inlet SO at WwTW | NY6290066400 | GB102076073981 | Irthing DS Crammel Linn Waterfall | RIVER IRTHING | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 633.34 | 115 | 114.75 | 4 (installed 2019) | 100 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1245
United Utilities | GILSLAND (BATH HOUSE) CSO (101VN) | Gilsland (Bath House) CSO | 017680314 | CAR0068 | SO | SO on sewer network | NY6340066530 | GB102076073981 | Irthing DS Crammel Linn Waterfall | RIVER IRTHING | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 15.37 | 25 | 18.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG1246
United Utilities | GILCRUX WWTW GILCR | GILCRUX WwTW | 017570069 | 17570069 | ST | Storm tank at WwTW | NY1110038360 | GB112075073640 | Ellen (lower) | BULLCLOSE BECK | N/A | Allonby | Not Applicable | Commissioned in 2017 - full year data expected | 4560.76 | 230 | 183 | 6 (installed 2017) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1247
United Utilities | GARSTANG STW | GARSTANG WwTW | 017260046 | 17260046 | ST | Storm tank at WwTW | SD4788042750 | GB112072065822 | Wyre DS Grizedale Brook confl | RIVER WYRE | N/A | Fleetwood | Not Applicable | Commissioned in 2020 - full year data expected | 1705.03 | 92 | 128.6667 | 3 (installed 2020) | 99.94 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1248
United Utilities | KEPPLE LANE(OVERFLOW C GARSTANG)CSO | Kepple Lane (Overflow 'C' Garstang) CSO | 017260029 | WYR0030 | SO | SO on sewer network | SD4883044700 | GB112072065822 | Wyre DS Grizedale Brook confl | RIVER WYRE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 449.66 | 91 | 73 | 3 (installed 2020) | 96.39 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1249
United Utilities | A6 JUNCTION OF CHURCHTOWN CSO | A6 Junction of Churchtown CSO | 017260074 | WYR0031 | SO | SO on sewer network | SD4570041150 | GB112072066250 | Wyre - conf R Brock to tidal | TIDAL RIVER WYRE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 168.27 | 50 | 57.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1250
United Utilities | SINGLETON PS | Singleton PS | 017290649 | WYR0083 | SO | Storm discharge at pumping station | SD3826037940 | GB112072066120 | Hillylaid Pool - Tidal Wyre | UNNAMED TRIB OF MAIN DYKE | N/A | Fleetwood | Not Applicable | Commissioned in 2020 - full year data expected | 295.91 | 56 | 34.3333 | 3 (installed 2020) | 99.9 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1251
United Utilities | EAST OF COUNCIL OFFICE | East of Council Offices CSO | 01WYR0039 | WYR0039 | SO | SO on sewer network | SD4937045420 | GB112072065822 | Wyre DS Grizedale Brook confl | RIVER WYRE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 305.5 | 71 | 65 | 3 (installed 2020) | 78.92 | Sensor failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1252
United Utilities | KENLIS STW | Kenlis PS | 017260145 | WYR0047 | SO | Storm discharge at pumping station | SD5079043860 | GB112072066220 | Calder (Wyre) | LITTLE CALDER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 727.39 | 103 | 80.3333 | 3 (installed 2020) | 97.28 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1253
United Utilities | SCORTON VILLAGE PUMPING STATION | Gubberford Lane PS | 017260047 | WYR0049 | SO | Storm discharge at pumping station | SD4998048260 | GB112072065821 | Wyre - Upper | RIVER WYRE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 572.56 | 82 | 72 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1254
United Utilities | GARSTANG RD/GREAT ECCLESTON PS | Garstang Rd, Great Eccleston PS (Site ID 52544) (WYR0051) | 01WYR0051 | WYR0051 | SO | Storm discharge at pumping station | SD4325040650 | GB112072066250 | Wyre - conf R Brock to tidal | RIVER WYER ESTUARY | N/A | Morcambe South | Not Applicable | Commissioned in 2016 - full year data expected | 655.45 | 116 | 86.5714 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1255
United Utilities | CALDER VALE PUMPING STATION | Calder Vale PS | 017290476 | WYR0078 | SO | Storm discharge at pumping station | SD5311045170 | GB112072066220 | Calder (Wyre) | RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 23.89 | 14 | 18.5 | 6 (installed 2017) | 99.99 | [5 empty] | UUG1256
United Utilities | THE AVENUE (CHURCHTOWN) CSO | The Avenue (churchtown) CSO | 017290551 | WYR0081 | SO | SO on sewer network | SD4877042970 | GB112072065822 | Wyre DS Grizedale Brook confl | RIVER WYRE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 72.33 | 10 | 9 | 3 (installed 2020) | 99.99 | [5 empty] | UUG1257
United Utilities | RIBBLESDALE DRIVE PS | Ribblesdale Drive PS | 017280304 | WYR0068 | SO | Storm discharge at pumping station | SD4876051400 | GB112072065880 | Cocker (Lune) | TRIB RIVER COCKER | N/A | N/A | Not Applicable | Dec 2023 | 0.02 | 1 |  | <1 yr (installed 2023) | 69.8925 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1258
United Utilities | FORMBY WASTEWATER TREATMENT WORKS | FORMBY WwTW | 016930108 | 16930108 | ST | Storm tank at WwTW | SD2971005900 | GB112069061442 | Alt DS Bull Bridge | RIVER ALT | N/A | Formby | Not Applicable | Commissioned in 2016 - full year data expected | 312.37 | 54 | 80.7143 | 7 (installed 2016) | 99.94 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1259
United Utilities | FLETCHERTOWN STW | FLETCHERTOWN WwTW | 017570014 | 17570014 | ST | Storm tank at WwTW | NY2125043500 | GB102075073480 | Crummock Beck u/s Holme Dub | CRUMMOCK BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 2230.9 | 163 | 214.6667 | 3 (installed 2020) | 100 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1260
United Utilities | MORICAMBE PARK PS 02540 | Moricambe Park PS | 017580248 | ALL0111 | SO | Storm discharge at pumping station | NY1282055840 | 90 |  | GREAT GUTTER ESTUARINE WATER | N/A | Silloth | Not Applicable | Commissioned in 2016 - full year data expected | 0.28 | 2 | 13.8571 | 7 (installed 2016) | 100 | [5 empty] | UUG1261
United Utilities | MANHOLE N20 E PARK DR CSO/SP DR PS | Manhole No. 20 off East Park Drive CSO / South Park Drive PS | 017260025 | BPL0007 | SO | SO on sewer network | SD3290035500 | GB112072066120 | Hillylaid Pool - Tidal Wyre | MARTON MERE VIA MAIN DYKE | N/A | Blackpool North | Not Applicable | Commissioned in 2016 - full year data expected | 0 | 0 | 0.14286 | 7 (installed 2016) | 99.98 | [5 empty] | UUG1262
United Utilities | SQUIRES GATE LANE | Squires Gate Lane | 01BPL0020 | BPL0020 | SO | SO on sewer network | SD3279032320 | GB112071065651 | Main Drain (Ribble) | SQUIRES GATE LANE DYKE | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1263
United Utilities | LENNOX GATE PUMPING STATION | Lennox Gate PS | 017180567 | BPL0022 | SO | Storm discharge at pumping station | SD3177533085 | GB112071065651 | Main Drain (Ribble) | IRISH SEA | N/A | Blackpool (South) | Not Applicable | Commissioned in 2016 - full year data expected | 30.96 | 42 | 20 | 7 (installed 2016) | 99.54 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1264
United Utilities | SOUTERGATE WWTW SOUTE SOUTE | SOUTERGATE WwTW | 017470020 | 17470020 | SO | Inlet SO at WwTW | SD2205081370 | 187 |  | SOUTERGATE BECK | N/A | Haverigg; Walney Biggar Bank; Walney West Shore; Walney Sandy Gap | Not Applicable | Commissioned in 2017 - full year data expected | 1798.71 | 110 | 107.8333 | 6 (installed 2017) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1265
United Utilities | MANCHESTER SQUARE PS | Manchester Square PS | 017160287 | BPL0039 | SO | Storm discharge at pumping station | SD3053035070 | GB641211630001 | Mersey Mouth | IRISH SEA | N/A | Blackpool North; Blackpool Central; Blackpool South; Bispham | Not Applicable | Commissioned in 2017 - full year data expected | 229.24 | 63 | 44.5 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1266
United Utilities | ANCHORSHOLME PS | Anchorsholme PS | 017160288 | BPL0040 | SO | Storm discharge at pumping station | SD2753441114 | GB641211630001 | Mersey Mouth | IRISH SEA | N/A | Bispham; Cleveleys; Fleetwood | Not Applicable | Commissioned in 2017 - full year data expected | 947.47 | 86 | 34 | 6 (installed 2017) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1267
United Utilities | SOUTERGATE VILLAGE PUMPING STATION | Soutergate Village Pumping Station (Site ID SOUPS) (LAK0094) | 017480359 | LAK0094 | SO | Storm discharge at pumping station | SD2205081371 | 187 |  | SOUTERGATE BECK | N/A | Haverigg; Walney Biggar Bank; Walney West Shore; Walney Sandy Gap | Not Applicable | Commissioned in 2017 - full year data expected | 238.22 | 17 | 6.6667 | 6 (installed 2017) | 97.26 | [5 empty] | UUG1268
United Utilities | MARSHSIDE PS | MARSHSIDE PS | 017370206 | LAK0095SO | SO | Storm discharge at pumping station | SD2315883393 | GB112074070130 | Duddon | Kirkby Pool | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1269
United Utilities | CHAIN LANE PUMPING STATION 19046 | Chain Lane PS | 01FYL0040 | FYL0040 | SO | Storm discharge at pumping station | SD3563035590 | GB112072066120 | Hillylaid Pool - Tidal Wyre | TRIB OF WYRE | N/A | Blackpool North | Not Applicable | Commissioned in 2016 - full year data expected | 55.34 | 50 | 35.5714 | 7 (installed 2016) | 99.48 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1270
United Utilities | SOUTHPORT WWTW | SOUTHPORT WwTW | 017030100 | 17030100 | ST | Storm tank at WwTW | SD3708020820 | 173 |  | CROSSENS POOL | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 59.57 | 13 | 33 | 6 (installed 2017) | 98.92 | [5 empty] | UUG1271
United Utilities | TRUNNAH ROAD PUMPING STATION | Trunnah Road PS | 017290503 | WYR0017 | SO | Storm discharge at pumping station | SD3386043240 | GB112072066160 | Hillylaid Pool - Main Dyke | ROYALS BROOK | N/A | Cleveleys | Not Applicable | Commissioned in 2016 - full year data expected | 31.68 | 5 | 48.2857 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1272
United Utilities | Watery Lane CSO | Watery Lane CSO | 16892508 | STH0061 | SO | SO on sewer network | SJ5345194161 | 176 |  | Sutton Mill Brook via CHAIN CAUL STORM CULVERT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 191.19 | 33 | 35.75 | 4 (installed 2019) | 98.19 | [5 empty] | UUG1273
United Utilities | IN FIELD POULTON M.H. 292 CSO | In Field, Poulton M/H 292 | 01WYR0020 | WYR0020 | SO | SO on sewer network | SD3528037971 | GB112072066120 | Hillylaid Pool - Tidal Wyre | UNNAMED TRIBUTARY OF MAIN DYKE | N/A | Fleetwood | Not Applicable | Commissioned in 2016 - full year data expected | 9.5 | 23 | 25.4286 | 7 (installed 2016) | 99.41 | [5 empty] | UUG1274
United Utilities | Hardhorn Road CSO | Hardhorn Road CSO | 17290544 | WYR0021 | SO | SO on sewer network | SD3622038690 | GB112072066120 | Hillylaid Pool - Tidal Wyre | Main Dyke - tributary of the Wyre | N/A | N/A | Not Applicable | Dec 2023 | 0.93 | 4 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1275
United Utilities | BACK OF WOODLAND DRIVE CSO | Back of Woodland Drive CSO | 01WYR0023 | WYR0023 | SO | SO on sewer network | SD3522038110 | GB112072066120 | Hillylaid Pool - Tidal Wyre | UNNAMED TRIBUTARY OF MAIN DYKE | N/A | Fleetwood | Not Applicable | Commissioned in 2016 - full year data expected | 0.2 | 2 | 2 | 7 (installed 2016) | 100 | [5 empty] | UUG1276
United Utilities | PRIORY ROAD CSO 392MO | Priory Road, Ulverston | 01LAK0005 | LAK0005 | SO | Storm discharge at pumping station | SD2973076700 | 181 |  | TRIB CARTER POOL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 87.03 | 44 | 22.8 | 5 (installed 2018) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1277
United Utilities | HIGHCROSS ROAD CSO | Highcross Road CSO | 017280298 | WYR0061 | SO | SO on sewer network | SD3622038690 | GB112072066120 | Hillylaid Pool - Tidal Wyre | MAIN DYKE TRIB OF WYRE ESTUARY | N/A | Fleetwood | Not Applicable | Commissioned in 2016 - full year data expected | 0.37 | 4 | 2.8571 | 7 (installed 2016) | 100 | [5 empty] | UUG1278
United Utilities | BARDSEA SPS(TOILET BLOCK) | Toilet Block Sewage PS | 017280254 | LAK0093 | SO | Storm discharge at pumping station | SD3021074320 | 181 |  | BARDSEA BECK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 1.79 | 3 | 10.1667 | 6 (installed 2017) | 100 | [5 empty] | UUG1279
United Utilities | WALTON-LE-DALE STW | WALTON-LE-DALE WwTW | 017160065 | 17160065 | ST | Storm tank at WwTW | SD5460028200 | 175 |  | RIVER RIBBLE ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 392.53 | 41 | 37 | 3 (installed 2020) | 99.77 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1280
United Utilities | HENNEL LANE CSO | Hennel Lane CSO | 017180616 | SRI0011 | SO | SO on sewer network | SD5518027980 | 175 |  | RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 540.24 | 62 | 61.75 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1281
United Utilities | GREGSON LANE AREA CSO 401WN | Gregson Lane Area CSO | 017160140 | SRI0014 | SO | SO on sewer network | SD5889026690 | 187 |  | MANY BROOKS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 294.83 | 111 | 110.25 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1282
United Utilities | HOLTS LANE DETENTION TANK | Holts Lane Detention Tanks | NPSWQD001283 | WYR0084 | SO | SO on sewer network | SD3552038670 | GB112072066120 | Hillylaid Pool - Tidal Wyre | MAIN DYKE | N/A | Fleetwood | Not Applicable | Commissioned in 2017 - full year data expected | 18.76 | 12 | 9.1667 | 6 (installed 2017) | 100 | [5 empty] | UUG1283
United Utilities | FAZAKERLEY WWTW | FAZAKERLEY WwTW | 016930112 | 16930112 | ST | Storm tank at WwTW | SJ3958096340 | GB112069060580 | Alt | RIVER ALT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 813.99 | 66 | 47.4 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1284
United Utilities | CROXTETH HALL LANE CSO 261QD | CROXTETH HALL LANE CSO | 01LIV0014 | LIV0014 | SO | SO on sewer network | SJ4050094950 | GB112069060580 | Alt | RIVER ALT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 3.63 | 5 | 3.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1285
United Utilities | FAILSWORTH WWTW | FAILSWORTH WwTW | 016983268 | 16983268 | SO | Inlet SO at WwTW | SJ8960099710 | GB112069061152 | Medlock (Lumb Brook to Irwell) | THE RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 215.32 | 60 | 58.3333 | 3 (installed 2020) | 99.97 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Resolved - Nov | Other investigation - non-WINEP/Green Recovery | UUG1286
United Utilities | FAILSWORTH WWTW | FAILSWORTH WwTW | 016983268 | 16983268 | ST | Storm tank at WwTW | SJ8960099710 | GB112069061152 | Medlock (Lumb Brook to Irwell) | THE RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 74.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1287
United Utilities | HOLT LANE FAILSWORTH SSO | Holt Lane (Failsworth ) SSO | 016982213 | OLD0122 | SO | SO on sewer network | SD9028000680 | GB112069061152 | Medlock (Lumb Brook to Irwell) | LORDS BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0.75 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1288
United Utilities | EMBLETON WWTW | EMBLETON WwTW | 017570038 | 17570038 | ST | Storm tank at WwTW | NY1795030530 | GB112075070500 | Wythop Beck | TRIB DUBWATH BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 3625.05 | 175 | 193.2 | 5 (installed 2018) | 100 |  |  | Performance - Infiltration | Scheduled | Stage 1c: Confirmed "hydraulic issue" | UUG1289
United Utilities | ELSWICK STW | ELSWICK WwTW | 017260053 | 17260053 | SO | Inlet SO at WwTW | SD4105038170 | GB112072066110 | Thistleton Brook | THISTLETON BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1483.68 | 267 | 289.3333 | 3 (installed 2020) | 100 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1290
United Utilities | BUNBURY STW | BUNBURY WwTW | 016810027 | 16810027 | SO | Inlet SO at WwTW | SJ5733058130 | GB112068060280 | Gowy and tribs (Source to Milton Brook) | RIVER GOWY | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 82.2 | 57 | 51 | 3 (installed 2020) | 99.32 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1291
United Utilities | FACTORY LANE CSO | Factory Lane CSO | 01SRI0023 | SRI0023 | SO | SO on sewer network | SD5399027460 | 175 |  | BOUNDARY BROOK TRIB RIV RIBBLE | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 176.07 | 38 | 31.5714 | 7 (installed 2016) | 98.29 | [5 empty] | UUG1292
United Utilities | MICKLE TRAFFORD PUMPING STATION | Mickle Trafford PS | 016892313 | CHE0028 | ST | Storm discharge at pumping station | SJ4408070700 | GB112068060260 | Stanney Mill Brook | TRIB OF STANNEY MILL BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1018.41 | 80 | 20 | 4 (installed 2019) | 99.8 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1293
United Utilities | MICKLE TRAFFORD PUMPING STATION | Mickle Trafford PS | 016892313 | CHE0028 | SO | Storm discharge at pumping station | SJ4408070700 | GB112068060260 | Stanney Mill Brook | TRIB OF STANNEY MILL BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 182.74 | 42 | 45.5 | 4 (installed 2019) | 99.84 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1294
United Utilities | RIVACRE VALLEY PARK CSO | Rivacre Valley Park CSO | 016891627 | ELL0007 | SO | SO on sewer network | SJ3853077990 | GB112068060350 | Rivacre Brook | RIVACRE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 14.83 | 7 | 72.5 | 4 (installed 2019) | 95.15 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1295
United Utilities | VALLEY DRIVE CSO | Rear of Valley Drive CSO | 01ELL0008 | ELL0008 | SO | SO on sewer network | SJ3795076560 | GB112068060350 | Rivacre Brook | RIVACRE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 19.08 | 14 | 10.25 | 4 (installed 2019) | 99.97 | [5 empty] | UUG1296
United Utilities | RIVACRE VALLEY PARK CSO | Rivacre Valley Park CSO (182OG) (ELL0010) | 01ELL0010 | ELL0010 | SO | SO on sewer network | SJ3835077970 | GB112068060350 | Rivacre Brook | RIVACRE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 102.7 | 40 | 46.75 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1297
United Utilities | CAUSEY WAY COMBINED SEWER OVERFLOW | Causey Way CSO | 017190839 | SRI0030 | SO | SO on sewer network | SD5404026650 | 175 |  | BOUNDARY BROOK | N/A | St Annes | Not Applicable | Commissioned in 2016 - full year data expected | 147.84 | 79 | 77.2857 | 7 (installed 2016) | 94.37 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1298
United Utilities | THORNTON ROAD ELLESMERE PORT CSO | Little Stanney SO | 016881595 | ELL0033 | SO | SO on sewer network | SJ4155074980 | GB112068060260 | Stanney Mill Brook | STANNEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 101.43 | 46 | 43 | 4 (installed 2019) | 97.15 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1299
United Utilities | WARRINGTON NORTH WWTW | WARRINGTON NORTH WwTW | 016983122 | 16983122 | SO | Inlet SO at WwTW | SJ5804086890 | 170 |  | MERSEY ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 52.12 | 16 | 35 | 4 (installed 2019) | 97.14 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG1300
United Utilities | EDENHALL VILLAGE & HOTEL WwTW | EDENHALL VILLAGE & HOTEL WwTW | 017670058 | 17670058 | SO | Inlet SO at WwTW | NY5630632611 | GB102076073940 | Eden - Eamont to tidal | A tributary of River Eden | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1377.15 | 137 | 149 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1301
United Utilities | ECCLES STW | ECCLES WwTW | 016940144 | 16940144 | SO | Inlet SO at WwTW | SJ7496097150 | GB112069061430 | Folly Brook and Salteye Brook. | SALTEYE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1071.82 | 139 | 141.75 | 4 (installed 2019) | 99.81 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1302
United Utilities | ECCLES STW | ECCLES WwTW | 016940144 | 16940144 | ST | Storm tank at WwTW | SJ7496097150 | GB112069061430 | Folly Brook and Salteye Brook. | SALTEYE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 501.46 | 56 | 83.25 | 4 (installed 2019) | 99.45 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1303
United Utilities | FIR TREE AVENUE PUMPING STATION | Fir Tree Avenue PS | 01SAL0001 | SAL0001 | SO | Storm discharge at pumping station | SD7247000210 | GB112069061090 | Shaw Brook | SNIGGLEY DITCH | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 26.01 | 11 | 10.6 | 5 (installed 2018) | 99.41 | [5 empty] | UUG1304
United Utilities | VICARS HALL LANE PS NO 2 | Vicars Hall Lane PS No. 1 & CSO | 016983333 | SAL0002 | SO | SO on sewer network | SD7170100361 | GB112069061090 | Shaw Brook | ELLEN BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 479.91 | 53 | 42.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1305
United Utilities | WINTON OUTFALL | Winton Outfall CSO | 016993656 | SAL0018 | SO | SO on sewer network | SJ7537097600 | GB112069061430 | Folly Brook and Salteye Brook. | SALTEYE BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 424.13 | 86 | 28.6667 | 3 (installed 2020) | 97.17 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1306
United Utilities | BENTCLIFFE WAY/WOOD ST CSO | Bentcliffe Way / Wood Street CSO | 01SAL0022 | SAL0022 | SO | SO on sewer network | SJ7815098360 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | GILDA BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.17 | 3 | 2.5 | 4 (installed 2019) | 99.53 | [5 empty] | UUG1307
United Utilities | BARTON ROAD PS & CSO | Barton Road No.1 PS & No.2 CSO | 016983337 | SAL0035 | SO | SO on sewer network | SD7509100090 | GB112069061430 | Folly Brook and Salteye Brook. | WORSLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 346.16 | 71 | 14.2 | 5 (installed 2018) | 99.97 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Scheduled | Other investigation - non-WINEP/Green Recovery | UUG1308
United Utilities | LIVERPOOL ROAD/NEWHALL AVENUE CSO | Liverpool Road/Newhall Avenue CSO | 01SAL0054 | SAL0054 | SO | SO on sewer network | SJ7530097480 | GB112069061430 | Folly Brook and Salteye Brook. | SALTEYE BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 32.77 | 61 | 64.3333 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1309
United Utilities | NEWEARTH ROAD CSO | Newearth Road CSO | 01SAL0061 | SAL0061 | SO | SO on sewer network | SD7267001650 | GB112069061090 | Shaw Brook | TRIBUTARY OF ELLEN BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 61.89 | 51 | 26.5 | 4 (installed 2019) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1310
United Utilities | PARK ST/SWINTON HALL ROAD CSO | Park Street/Swinton Hall Road | EPRTB3192VK | SAL0101 | SO | SO on sewer network | SD7804001100 | GB112069061430 | Folly Brook and Salteye Brook. | TRIB FOLLY BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 4.27 | 12 | 14.6667 | 3 (installed 2020) | 65.73 | Comms failure / issue | Resolved - January after reporting year |  |  |  | UUG1311
United Utilities | WALKDEN RD HOLYOAKE RD CSO 37045 | Walkden Road/Hoylake Road CSO | 016983330 | SAL0113 | SO | SO on sewer network | SD7384002760 | GB112069061430 | Folly Brook and Salteye Brook. | WORSLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected |  |  | 31.8 | 5 (installed 2018) | 0 | Installation set-up/design issue | Scheduled |  |  |  | UUG1312
United Utilities | GREENLEACH LANE CSO | Greenleach Lane CSO | 016993659 | SAL0125 | SO | SO on sewer network | SD7520001310 | GB112069061430 | Folly Brook and Salteye Brook. | KEMPNOUGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 25.79 | 14 | 13.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1313
United Utilities | GLYNRENE DRIVE CSO | Glynrene Drive CSO | EPRSB3397WJ | SAL0114 | SO | SO on sewer network | SD7598002460 | GB112069061430 | Folly Brook and Salteye Brook. | TRIB OF KEMPNOUGH BROOK VI SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0.33333 | 3 (installed 2020) | 100 | [5 empty] | UUG1314
United Utilities | BRADFORD ROAD | Swinton Eccles Transfer Sewer Stage 1 | 01SAL0144 | SAL0144 | SO | SO on sewer network | SJ7742099920 | GB112069061430 | Folly Brook and Salteye Brook. | Salteye Brook | N/A | N/A | Not Applicable | Dec 2023 | 14.7 | 19 |  | <1 yr (installed 2023) | 97.4576 | [5 empty] | UUG1315
United Utilities | IN FIELDS REAR OF 36 EAST DRIVE CSO | In fields at rear of 36 East Drive CSO | 016982743 | SAL0153 | SO | SO on sewer network | SD7886001310 | GB112069061430 | Folly Brook and Salteye Brook. | FOLLY BROOK VIA A SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 15.67 | 14 | 12.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG1316
United Utilities | BOOTHS BANK FARM CSO (37046) | Booths Bank Farm CSO | 016982745 | SAL0156 | SO | SO on sewer network | SD7320000500 | GB112069061090 | Shaw Brook | SHAW BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 40.6 | 3 (installed 2020) | 46.81 | Comms failure / issue | Resolved - January after reporting year | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1317
United Utilities | DORCHESTER RD ADJ NO 182 MANCH CSO | Dorchester Rd, adj 182 Manchester Rd | 016982744 | SAL0154 | SO | SO on sewer network | SD7770000620 | GB112069061430 | Folly Brook and Salteye Brook. | TRIB FOLLY BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0 | 4 (installed 2019) | 99.93 | [5 empty] | UUG1318
United Utilities | OPPOSITE NO 1 GRANBY ROAD CSO | Opposite No.1 Granby Road CSO | 016982647 | SAL0169 | SO | SO on sewer network | SD7630000880 | GB112069061430 | Folly Brook and Salteye Brook. | TRIB SINDSLEY BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 33.7 | 62 | 66.25 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1319
United Utilities | BARTON LANE COMBINED SEWER OVERFLOW | Barton Lane/Fountain Street CSO | 016982648 | SAL0176 | SO | SO on sewer network | SJ7677097680 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 10.7 | 14 | 10.75 | 4 (installed 2019) | 100 | [5 empty] | UUG1320
United Utilities | REAR OF 47 VENDALE AVE CSO (379AE) | Rear of 47 Vendale Avenue | 016982746 | SAL0162 | SO | SO on sewer network | SD7695000600 | GB112069061430 | Folly Brook and Salteye Brook. | DEANS BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 3.33 | 23 | 7.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG1321
United Utilities | REAR OF 256 DALES BROW CSO | Rear of 256 Dales Brow CSO | 016982884 | SAL0184 | SO | SO on sewer network | SD7705900757 | GB112069061430 | Folly Brook and Salteye Brook. | DEANS BROOK TRIB FOLLY BK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 28.17 | 43 | 30.5 | 4 (installed 2019) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1322
United Utilities | EAGLESFIELD WWTW EAGLE | EAGLESFIELD WwTW | 017570037 | 17570037 | ST | Storm tank at WwTW | NY0975028480 | GB112075070400 | Cocker - conf Whit Beck to conf Derwent | DUBBS GUTTER | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 1812.98 | 151 | 245.1667 | 6 (installed 2017) | 99.83 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1323
United Utilities | DEANSCALES PS & CSO | Deanscales PS and CSO | 017570034 | ALL0121 | SO | Storm discharge at pumping station | NY0922026470 | GB112075070540 | Marron | TRIB OF FAR STOCK BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 775.03 | 102 | 108.75 | 4 (installed 2019) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1324
United Utilities | DUNHAM MASSEY STW | DUNHAM MASSEY WwTW | 016940003 | 16940003 | ST | Storm tank at WwTW | SJ7269087540 | GB112069061382 | Bollin (Ashley Mill to Manchester Ship Canal) | RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 543.5 | 94 | 18.8 | 5 (installed 2018) | 99.43 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1325
United Utilities | DUNHAM MASSEY OUTFALL CSO (451SS) | Dunham Massey Outfall SSO | 01TRA0079 | TRA0079 | SO | SO on sewer network | SJ7269087541 | GB112069061382 | Bollin (Ashley Mill to Manchester Ship Canal) | RIVER BOLLIN VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 231.27 | 75 | 58.3333 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1326
United Utilities | DUKINFIELD WWTW | DUKINFIELD WwTW | 016940087 | 16940087 | SO | Inlet SO at WwTW | SJ9326096730 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 86.76 | 29 | 45.6667 | 3 (installed 2020) | 86.78 | Comms failure / issue | Resolved - January after reporting year | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1327
United Utilities | DUKINFIELD WWTW | DUKINFIELD WwTW | 016940087 | 16940087 | ST | Storm tank at WwTW | SJ9326096730 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1432.69 | 125 | 118.3333 | 3 (installed 2020) | 99.97 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Scheduled | Other investigation - non-WINEP/Green Recovery | UUG1328
United Utilities | ASHTON OLD RD MANSHAW ST CSO 281CD | ASHTON OLD ROAD / MANSHAW STREET CSO | 01MAN0204 | MAN0204 | SO | SO on sewer network | SJ9014097320 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MOSS BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.47 | 10 | 17.2 | 5 (installed 2018) | 100 | [5 empty] | UUG1329
United Utilities | RASSBOTTOM STREET CSO | Rassbottom Street CSO | 016940471 | TAM0039 | SO | SO on sewer network | SJ9588098580 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2.32 | 4 | 4.25 | 4 (installed 2019) | 99.72 | [5 empty] | UUG1330
United Utilities | WHARF STREET CSO 44184 | Wharf Street CSO | 016940472 | TAM0040 | SO | SO on sewer network | SJ9347898194 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | River Tame | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 288.5 | 78 | 68.6 | 5 (installed 2018) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1331
United Utilities | ARGYL STREET | Argyll Street CSO | 01TAM0046 | TAM0046 | SO | SO on sewer network | SJ9521099000 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | COCK BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1332
United Utilities | EDWARD STREET | Edward Street (Dunkinfield) CSO | 01TAM0074 | TAM0074 | SO | SO on sewer network | SJ9355096350 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | TRIB OF RIVER TAME VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 13.6 | 29 | 35.6667 | 3 (installed 2020) | 94.76 | [5 empty] | UUG1333
United Utilities | CHEETHAM HILL ROAD CSO | Cheetham Hill Road CSO | 01TAM0078 | TAM0078 | SO | SO on sewer network | SJ9489096610 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | JOHNSON BROOK | N/A | N/A | Not Applicable | Dec 2023 | 12.31 | 31 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1334
United Utilities | BUCKTON VALE ROAD CSO | Buckton Vale Road CSO | 016993735 | TAM0093 | SO | SO on sewer network | SD9768000050 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | A CULVERTED TRIB TO RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.07 | 1 | 2.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1335
United Utilities | STAMFORD ST CSO (442SC) | Stamford Street CSO | 016993724 | TAM0094 | SO | SO on sewer network | SJ9789099680 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | SWINESHAW BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.1 | 1 | 2 | 3 (installed 2020) | 93.43 | [5 empty] | UUG1336
United Utilities | OFF GROVE ROAD CSO 44217 | Off Grove Road CSO | 016993726 | TAM0095 | SO | SO on sewer network | SJ9765899782 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | CLVRT SECT SWINESHAW BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 3.13 | 11 | 30.2 | 5 (installed 2018) | 99.99 | [5 empty] | UUG1337
United Utilities | GROVE ROAD CSO | Grove Road CSO | 016993678 | TAM0096 | SO | SO on sewer network | SJ9748099950 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 422.06 | 98 | 84.3333 | 3 (installed 2020) | 91.25 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1338
United Utilities | KNOWLE STREET CSO 442BX | Knowle Street CSO | 016993732 | TAM0097 | SO | SO on sewer network | SJ9666098600 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | THE RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 3 | 5 (installed 2018) | 100 | [5 empty] | UUG1339
United Utilities | HUDDERSFIELD ROAD CSO (449BD) | Huddersfield Road CSO | 016993729 | TAM0098 | SO | SO on sewer network | SJ9723098810 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | CULVERT TO RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 2.07 | 9 | 22.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG1340
United Utilities | CORPORATION STREET | Corporation Street CSO | 01TAM0099 | TAM0099 | SO | SO on sewer network | SJ9655098550 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 362.78 | 119 | 106.3333 | 3 (installed 2020) | 99.37 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1341
United Utilities | MARKET STREET/TRINITY STREET CSO | MARKET STREET / TRINITY STREET CSO | 01TAM0100 | TAM0100 | SO | SO on sewer network | SJ9635098600 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | RIVER TAME | N/A | N/A | Not Applicable | Dec 2023 | 148.47 | 58 |  | <1 yr (installed 2023) | 97.7444 | [5 empty] | UUG1342
United Utilities | CUMBERLAND STREET CSO | Cumberland Street CSO | 016993736 | TAM0101 | SO | SO on sewer network | SJ9590098800 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | CULVERT TO THE RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2.77 | 14 | 14.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1343
United Utilities | STAMFORD GROVE CSO | STAMFORD GROVE CSO | 01TAM0102 | TAM0102 | SO | SO on sewer network | SJ9565098980 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME VIA A CULVERT | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.07 | 1 | 1 | 3 (installed 2020) | 91.5 | [5 empty] | UUG1344
United Utilities | TRINITY ST/DEAN ST | Trinity Street/Dean Street CSO | 016993730 | TAM0103 | SO | SO on sewer network | SJ9636098530 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | THE RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.1 | 1 | 4 | 3 (installed 2020) | 100 | [5 empty] | UUG1345
United Utilities | MELBOURNE STREET | Melbourne Street CSO | 016993731 | TAM0105 | SO | SO on sewer network | SJ9628098530 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | THE RIVER TAME | N/A | N/A | Not Applicable | Dec 2023 | 0.3 | 3 |  | <1 yr (installed 2023) | 97.3545 | [5 empty] | UUG1346
United Utilities | TAME STREET/PARK ROAD CSO | Tame Street/Park Road CSO | 01TAM0109 | TAM0109 | SO | SO on sewer network | SJ9539098160 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1347
United Utilities | HANOVER STREET CSO | HANOVER STREET CSO | 01TAM0111 | TAM0111 | SO | SO on sewer network | SJ9590098820 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | CULVERT TO RIVER TAME | N/A | N/A | Not Applicable | Dec 2023 | 73.2 | 62 |  | <1 yr (installed 2023) | 97.8836 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1348
United Utilities | STOCKS LANE CSO | STOCKS LANE CSO | 01TAM0113 | TAM0113 | SO | SO on sewer network | SJ9741098290 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | STOCKS BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 2 | 3 (installed 2020) | 100 | [5 empty] | UUG1349
United Utilities | 212 MOTTRAM ROAD CSO | 212 Mottram Road CSO | 01TAM0114 | TAM0114 | SO | SO on sewer network | SJ9721097300 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | TRIB OF ACRES BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 1.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG1350
United Utilities | OFF HUDDERSFIELD ROAD CSO 442JA | Off Huddersfield Road CSO | 016993725 | TAM0116 | SO | SO on sewer network | SJ9785099480 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | CLVRT SEC UNNAMED TRIB RVRTAME | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.23 | 3 | 28.6 | 5 (installed 2018) | 96.11 | [5 empty] | UUG1351
United Utilities | ST GEORGE STREET/HANOVER STREET CSO | St. George Street/Hanover Street CSO | 01TAM0118 | TAM0118 | SO | SO on sewer network | SJ9591098541 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Dec 2023 | 2803.57 | 153 |  | <1 yr (installed 2023) | 97.076 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1352
United Utilities | CANAL BANK TRANSFORMER HSE CSO | Canal Bank near Transformer House CSO | 01TAM0122 | TAM0122 | SO | SO on sewer network | SJ9752099910 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | SWINESHAW BROOK TRIB RVR TAME | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 56.6 | 56 | 53 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1353
United Utilities | BINNS STREET CSO | BINNS STREET CSO | 01TAM0123 | TAM0123 | SO | SO on sewer network | SJ9534098130 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Dec 2023 | 0.17 | 2 |  | <1 yr (installed 2023) | 98.6547 | [5 empty] | UUG1354
United Utilities | FERN BANK CSO | FERN BANK CSO | 01TAM0126 | TAM0126 | SO | SO on sewer network | SJ9723097940 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | STOCKS BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 7.93 | 36 | 55 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1355
United Utilities | HOUGH HILL ROAD/GRASSCROFT ST CSO | HOUGH HILL ROAD / GRASSCROFT STREET CSO | 01TAM0132 | TAM0132 | SO | SO on sewer network | SJ9645098180 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 1 | 3 (installed 2020) | 100 | [5 empty] | UUG1356
United Utilities | DUKINFIELD OUTFALL SEWER CSO 441SM | Dukinfield Outfall Sewer CSO | 01TAM0150 | TAM0150 | SO | SO on sewer network | SJ9327096700 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 2.97 | 11 | 10.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG1357
United Utilities | ILLINGWORTH AVENUE | Illingworth Avenue CSO | 016982691 | TAM0161 | SO | SO on sewer network | SJ9727098430 | GB112069061111 | Tame (Chew Brook to Swineshaw Brook) | STOCKS BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1358
United Utilities | LUMB LANE (AUDENSHAW) CSO & DET TNK | Lumb Lane (Audenshaw) CSO and Detention Tank | 016982921 | TAM0170 | SO | Storm discharge at pumping station | SJ9140097501 | GB112069060940 | Culverted Gore Brook | Culverted section of Gore Brook | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 34.21 | 7 | 10.75 | 4 (installed 2019) | 100 | [5 empty] | UUG1359
United Utilities | BROOMSTAIR ROAD CSO | Broomstair Road CSO | 016982919 | TAM0171 | SO | SO on sewer network | SJ9304096520 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 237.65 | 55 | 64.25 | 4 (installed 2019) | 88.38 | Capital / maintenance works affect EDM operation | Resolved - Oct | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1360
United Utilities | MANSHAW ROAD CSO | Manshaw Road CSO | 016982836 | TAM0174 | SO | SO on sewer network | SJ9014397126 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MOSS BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 35.9 | 13 | 30.25 | 4 (installed 2019) | 99.73 | [5 empty] | UUG1361
United Utilities | DUFTON VILLAGE STW | DUFTON WwTW | 017670010 | 17670010 | SO | Inlet SO at WwTW | NY6879025320 | GB102076070960 | Swindale Beck nr Dufton | MILL BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 38.36 | 6 | 27 | 4 (installed 2019) | 99.73 | [5 empty] | UUG1362
United Utilities | DUBWATH WASTEWATER TREATMENT WORKS | DUBWATH WwTW | 017570036 | 17570036 | SO | Inlet SO at WwTW | NY2001031190 | GB112075070500 | Wythop Beck | DUBWATH BECK | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 807.83 | 129 | 98.8571 | 7 (installed 2016) | 99.43 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1363
United Utilities | DOVENBY WWTW DOVEN | Dovenby Waste water Treatment Works (DOVEN) (017570035) | 017570035 | 17570035 | ST | Storm tank at WwTW | NY0895032850 | GB112075073570 | Broughton Beck | DOVENBY BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 240.31 | 37 | 51 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1364
United Utilities | COALPIT WOOD CSO | Coal Pitt Wood CSO | 017580316 | ALL0019 | SO | SO on sewer network | NY0915033110 | GB112075073570 | Broughton Beck | DOVENBY BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 89.13 | 44 | 44.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1365
United Utilities | DENT STW | DENT WwTW | 017270015 | 17270015 | SO | Inlet SO at WwTW | SD7021087350 | GB112072071680 | Dee - conf Deepdale Bk to conf Rawthey | TRIB RIVER DEE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 198.86 | 78 | 115.3333 | 3 (installed 2020) | 99.99 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1366
United Utilities | DEARHAM WASTEWATER TREATMENT WORKS | DEARHAM WwTW | 017570068 | 17570068 | SO | Inlet SO at WwTW | NY0704036760 | GB112075073640 | Ellen (lower) | RIVER ELLEN | N/A | Allonby | Not Applicable | Commissioned in 2017 - full year data expected | 726.6 | 119 | 167 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1367
United Utilities | TALLENTIRE PUMPING STATION | Tallentire (West) PS | 017570058 | ALL0092 | SO | Storm discharge at pumping station | NY1003235482 | GB112075073570 | Broughton Beck | UNNAMED TRIB OF BROUGHTON BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 500.84 | 63 | 74.2 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1368
United Utilities | DAVYHULME WWTW | DAVYHULME WwTW | 016940143 | 16940143 | ST | Storm tank at WwTW | SJ7480096460 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1447.3 | 85 | 28.3333 | 3 (installed 2020) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1369
United Utilities | 92 BURNLEY ROAD CSO 081HP | 92 Burnley Road CSO | 01BUR0010 | BUR0010 | SO | SO on sewer network | SD8225028070 | GB112069064680 | Limy Water | LIMY WATER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 104.27 | 29 | 46.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1370
United Utilities | POYNTON BALANCING TANK | Field No. XXX, Mill Hill, Poynton CSO | 01MAC0051 | MAC0051 | SO | SO on sewer network | SJ9158085330 | GB112069060940 | Micker Brook | NORBURY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1203.89 | 88 | 81 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1371
United Utilities | BARNABY RD CSO | Barnaby Road CSO | 016983005 | MAC0163 | SO | SO on sewer network | SJ9148083790 | GB112069060900 | Poynton Brook | POYNTON BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.7 | 1 | 2.75 | 4 (installed 2019) | 100 | [5 empty] | UUG1372
United Utilities | JULIA SREETT CSO | Julia Street CSO | EPRQB3590DE | MAN0005 | SO | SO on sewer network | SJ8357099240 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 696.37 | 104 | 103.5 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1373
United Utilities | CENTRAL AVENUE CSO | Central Avenue CSO | 01MAN0008 | MAN0008 | SO | SO on sewer network | SD8541001790 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.63 | 3 | 6.8 | 5 (installed 2018) | 100 | [5 empty] | UUG1374
United Utilities | PLATT LANE COMBINED SEWER OVERFLOW | Platt Lane CSO | 016941067 | MAN0017 | SO | SO on sewer network | SJ8490094400 | GB112069061060 | Platt Brook (Source to Fallowfield Bk) | PLATT BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.23 | 1 | 0.75 | 4 (installed 2019) | 100 | [5 empty] | UUG1375
United Utilities | ASPIN LANE CSO 281CJ | ASPIN LANE CSO | 01MAN0031 | MAN0031 | SO | SO on sewer network | SJ8421099220 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 16.47 | 43 | 64.4 | 5 (installed 2018) | 98.48 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1376
United Utilities | ROLLESTON AVENUE/BUTLER STREET CSO | ROLLESTON AVENUE / BUTLER STREET CSO | 01MAN0032 | MAN0032 | SO | SO on sewer network | SJ8558098902 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.97 | 10 | 8 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1377
United Utilities | PRINCES PRKWAY/M60 CSO 28051 | Princess Parkway/M60 CSO | 016942049 | MAN0020 | SO | SO on sewer network | SJ8254191081 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 250.03 | 50 | 42.1667 | 6 (installed 2017) | 97.65 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1378
United Utilities | DANTZIC ST WARFORD ST CSO 288A7 | DANTZIC STREET / WARFORD STREET CSO | 01MAN0039 | MAN0039 | SO | SO on sewer network | SJ8460099540 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.1 | 1 | 48.8 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1379
United Utilities | SMEDLEY ROAD CSO | Smedley Road CSO | 01MAN0042 | MAN0042 | SO | SO on sewer network | SD8524000350 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 35.18 | 28 | 31.8 | 5 (installed 2018) | 99.98 | [5 empty] | UUG1380
United Utilities | ROCHDALE/COLLYHURST ROAD CSO | Rochdale/Collyhurst Road CSO | 01MAN0050 | MAN0050 | SO | SO on sewer network | SD8545000080 | GB112069061131 | Irk (Wince to Irwell) | CULV'TED SECTION OF MOSS BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 9.03 | 17 | 50.5 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1381
United Utilities | BEAUMONT BUILDING CSO 28049 | Beaumont Building, Jnt New Bridge Street / Great Ducie Street CSO | 016993837 | MAN0051 | SO | SO on sewer network | SJ8368099050 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 73.8 | 45 | 32.2 | 5 (installed 2018) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1382
United Utilities | SHERBORNE STREET CSO | Sherborne Street CSO | 016993836 | MAN0052 | SO | SO on sewer network | SJ8346099322 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 40.7 | 36 | 46 | 5 (installed 2018) | 93.48 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1383
United Utilities | BUTLER STREET/WOODWARD STREET CSO | Butler Street/Woodward Street CSO | 01MAN0038 | MAN0038 | SO | SO on sewer network | SJ8558095740 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 7.6 | 5 (installed 2018) | 100 | [5 empty] | UUG1384
United Utilities | QUEENS ROAD COMBINED SEWER OVERFLOW | QUEENS ROAD CSO | NPSWQD010957 | MAN0055 | SO | SO on sewer network | SD8575000490 | GB112069061131 | Irk (Wince to Irwell) | MOSS BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 19.55 | 42 | 35.5 | 4 (installed 2019) | 99.99 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1385
United Utilities | FAIRY LANE CSO 281T3 | FAIRY LANE CSO | 01MAN0066 | MAN0066 | SO | SO on sewer network | SJ8346099321 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.33 | 2 | 4.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1386
United Utilities | LORD NORTH STREET/CLIFTON ST CSO | LORD NORTH STREET / CLIFTON STREET CSO | 01MAN0069 | MAN0069 | SO | SO on sewer network | SJ8662099660 | GB112069061152 | Medlock (Lumb Brook to Irwell) | SHOOTERS BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.87 | 12 | 33.25 | 4 (installed 2019) | 100 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG1387
United Utilities | KINGSBRIDGE ROAD CSO (289BQ) | Kingsbridge Road CSO | 01MAN0071 | MAN0071 | SO | SO on sewer network | SD8546001280 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.03 | 1 | 23.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG1388
United Utilities | ROCHDALE ROAD/EGGINGTON STREET CSO | ROCHDALE ROAD / EGGINGTON STREET CSO | 01MAN0058 | MAN0058 | SO | SO on sewer network | SD8543000100 | GB112069061131 | Irk (Wince to Irwell) | MOSTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.63 | 3 | 7.25 | 4 (installed 2019) | 100 | [5 empty] | UUG1389
United Utilities | WATERLOO ST CRESCENT RD CSO | Waterloo Street/Crescent Road CSO | 01MAN0074 | MAN0074 | SO | SO on sewer network | SD8537001580 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 32.17 | 41 | 38.4 | 5 (installed 2018) | 99.99 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1390
United Utilities | CLEVELAND RD DELAUNAY RD CSO 288NJ | Cleveland/Delauney's Road CSO | 01MAN0078 | MAN0078 | SO | SO on sewer network | SD8505102790 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 102.23 | 77 | 62 | 5 (installed 2018) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1391
United Utilities | QUEENS RD/HARDHAM VALE CSO | Queens Road/Hendham Vale CSO | 016993692 | MAN0081 | SO | SO on sewer network | SD8528000660 | GB112069061131 | Irk (Wince to Irwell) | THE RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1 | 11 | 11.75 | 4 (installed 2019) | 100 | [5 empty] | UUG1392
United Utilities | HENDHAM VALE CSO | Hendham Vale CSO | 016993691 | MAN0072 | SO | SO on sewer network | SD8514000960 | GB112069061131 | Irk (Wince to Irwell) | THE RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0 | 4 (installed 2019) | 100 | [5 empty] | UUG1393
United Utilities | MONSALL ROAD (J SEWER) CSO (282SF) | MONSALL ROAD (J SEWER) CSO | 01MAN0086 | MAN0086 | SO | SO on sewer network | SD8613400952 | GB112069061131 | Irk (Wince to Irwell) | CULVERTED TRIB OF MOSTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.7 | 4 | 6.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG1394
United Utilities | WINDSOR ROAD/WINTERDYNE STREET CSO | WINDSOR ROAD / WINTERDYNE STREET CSO | 01MAN0082 | MAN0082 | SO | SO on sewer network | SD8618001260 | GB112069061131 | Irk (Wince to Irwell) | MOSTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 9.3 | 6 | 2 | 4 (installed 2019) | 96.61 | [5 empty] | UUG1395
United Utilities | LATHBURY ROAD ADJ TO FOOTPATH CSO | Lathbury Road (Adjacent to the footpath) Combined Sewer Overflow | 01MAN0087 | MAN0087 | SO | SO on sewer network | SD8604000860 | GB112069061131 | Irk (Wince to Irwell) | MOSTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.07 | 1 | 1.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1396
United Utilities | VICTORIA AVENUE/RIVER IRK CSO | VICTORIA AVENUE/RIVER IRK CSO | 01MAN0094 | MAN0094 | SO | SO on sewer network | SD8404004050 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 5.83 | 11 | 7.75 | 4 (installed 2019) | 100 | [5 empty] | UUG1397
United Utilities | POTTERS LANE CSO | POTTERS LANE CSO | 01MAN0095 | MAN0095 | SO | SO on sewer network | SD8630001140 | GB112069061131 | Irk (Wince to Irwell) | CULVERTED SECTION MOSTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 21.87 | 33 | 97.75 | 4 (installed 2019) | 96.36 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1398
United Utilities | MIDDLETON ROAD/VICTORIA AVENUE CSO | MIDDLETON ROAD / VICTORIA AVENUE CSO | 01MAN0096 | MAN0096 | SO | SO on sewer network | SD8386004060 | GB112069061131 | Irk (Wince to Irwell) | TRIBUTARY OF RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 17.17 | 7 | 72.5 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1399
United Utilities | VICTORIA AVENUE/GLENBROOK CSO | Victoria Avenue/Glenbrook CSO | 016993670 | MAN0093 | SO | SO on sewer network | SD8404004060 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 4.25 | 4 (installed 2019) | 100 | [5 empty] | UUG1400
United Utilities | JUNCTION OF GRAVER LN ELSMA RD CSO | Junction of GRAVER LANE and ELSMA ROAD CSO | 01MAN0104 | MAN0104 | SO | SO on sewer network | SJ8896099500 | GB112069061152 | Medlock (Lumb Brook to Irwell) | BERRY BROW CULVERT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.97 | 4 | 2.25 | 4 (installed 2019) | 100 | [5 empty] | UUG1401
United Utilities | PARROTT STREET/BROMLOW STREET CSO | PARROT STREET / BROMLOW STREET CSO | 01MAN0107 | MAN0107 | SO | SO on sewer network | SJ8779097891 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | CORN BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 22.9 | 21 | 15 | 4 (installed 2019) | 100 | [5 empty] | UUG1402
United Utilities | ASSHETON ROAD CSO 281CA | ASSHETON ROAD CSO | 01MAN0108 | MAN0108 | SO | SO on sewer network | SJ8896099510 | GB112069061152 | Medlock (Lumb Brook to Irwell) | CLVRT TRIB OF RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 14.9 | 20 | 77 | 5 (installed 2018) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1403
United Utilities | SOUTH OF BLACKLEY NEW ROAD CSO | Blackley New Road CSO | 016993799 | MAN0110 | SO | SO on sewer network | SD8390003150 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 123.23 | 28 | 41.5 | 4 (installed 2019) | 97.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1404
United Utilities | SOUTH OF BLACKLEY NEW ROAD CSO | BLACKLEY NEW ROAD CSO | 01MAN0111 | MAN0111 | SO | SO on sewer network | SD8390003150 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 31.1 | 51 | 99.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1405
United Utilities | MILL BROW/BLACKLEY NEW ROAD CSO | Mill Brow/Blackley Road CSO | 016993671 | MAN0112 | SO | SO on sewer network | SD8520502856 | GB112069061131 | Irk (Wince to Irwell) | A CULVERTED SECTION RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 48.83 | 57 | 39.25 | 4 (installed 2019) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1406
United Utilities | ROCHDALE RD/ALFRED ST CSO | Rochdale Road/Alfreton Street CSO | 016993737 | MAN0116 | SO | SO on sewer network | SD8542001801 | GB112069061131 | Irk (Wince to Irwell) | THE RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 5.43 | 14 | 12.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1407
United Utilities | CLEVELAND RD DELAUNEYS RD CSO 281KK | Cleveland Road/Delaunays CSO | 016993738 | MAN0117 | SO | SO on sewer network | SD8500002810 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 4.67 | 13 | 12.2 | 5 (installed 2018) | 99.99 | [5 empty] | UUG1408
United Utilities | MOSTON LANE/ROCHDALE ROAD CSO | Moston Lane/Rochdale Road CSO | NPSWQD010701 | MAN0123 | SO | SO on sewer network | SD8542001800 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 105.2 | 59 | 47 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1409
United Utilities | GLENBROOK RD EXTER RD CSO 281VU | Glenbrook Road/Dexter Road CSO | 01MAN0125 | MAN0125 | SO | SO on sewer network | SD8415004420 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2.17 | 13 | 23 | 5 (installed 2018) | 100 | [5 empty] | UUG1410
United Utilities | DEXTER RD HEATON PARK RD CSO | Dexter Road/Heaton Park Road CSO | 016993739 | MAN0126 | SO | SO on sewer network | SD8415004470 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.8 | 8 | 12.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1411
United Utilities | BRENTFORD STREET CSO | BRENTFORD STREET CSO | 01MAN0127 | MAN0127 | SO | SO on sewer network | SD8610001200 | GB112069061131 | Irk (Wince to Irwell) | UNNAMED WATERCOURSE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 23.6 | 5 (installed 2018) | 97.75 | [5 empty] | UUG1412
United Utilities | MIDDLETON OLD ROAD CSO | Middleton Old Road CSO (Site ID - 28064/28CSO143) | NPSWQD010702 | MAN0135 | SO | SO on sewer network | SD8541002230 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 288.2 | 83 | 67.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1413
United Utilities | LATHBURY ROAD/SILCHESTER DRIVE CSO | LATHBURY ROAD / SILCHESTER DRIVE CSO | 01MAN0136 | MAN0136 | SO | SO on sewer network | SD8583500640 | GB112069061131 | Irk (Wince to Irwell) | MOSTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 3.93 | 14 | 13.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1414
United Utilities | CHUDDLEIGH ROAD CSO | Chudleigh Road CSO | 016993672 | MAN0140 | SO | SO on sewer network | SD8455002830 | GB112069061131 | Irk (Wince to Irwell) | THE RIVER IRK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1073.42 | 74 | 54.75 | 4 (installed 2019) | 99.91 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1415
United Utilities | BANK STREET CSO | BANK STREET STORAGE TANK CSO (28CSO123) | 016982847 | MAN0102 | SO | SO on sewer network | SJ8749099230 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1416
United Utilities | ROCHDALE RD/COLLYHURST | Rochdale Road/Collyhurst CSO | 016993740 | MAN0150 | SO | SO on sewer network | SD8533000020 | GB112069061131 | Irk (Wince to Irwell) | THE RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 768.8 | 135 | 33.75 | 4 (installed 2019) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1417
United Utilities | VICTORIA BRIDGE STREET CSO (282WL) | Victoria Bridge Street CSO | 01MAN0155 | MAN0155 | SO | SO on sewer network | SJ8377098690 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 26.63 | 43 | 25.3333 | 3 (installed 2020) | 98.21 |  |  | Data collection - EDM non-representative location | Resolved - Jun |  | UUG1418
United Utilities | BLACKFRIARS STREET CSO 283J1 | BLACKFRIARS STREET CSO | 01MAN0156 | MAN0156 | SO | SO on sewer network | SJ8368098590 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.5 | 5 | 27 | 5 (installed 2018) | 90.33 | [5 empty] | UUG1419
United Utilities | LONG MILLGATE CSO | Long Millgate_Near Manchester Cathedral Gardens_CSO | 016993741 | MAN0160 | SO | SO on sewer network | SJ8400098910 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 23.53 | 5 | 2 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1420
United Utilities | MILLER STREET/CORPORATION ST CSO | Miller St/Corporation St CSO | 01MAN0161 | MAN0161 | SO | SO on sewer network | SJ8414099060 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Dec 2023 | 0.37 | 3 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1421
United Utilities | CHARLES ST PRINCESS ST CSO 28116 | Charles Street/Princess Street CSO | 01MAN0166 | MAN0166 | SO | SO on sewer network | SJ8433097510 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1335 | 70 | 22 | 5 (installed 2018) | 98.21 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1422
United Utilities | WATER STREET/LIVERPOOL ROAD CSO | Water Street/Liverpool Road CSO | 016993597 | MAN0169 | SO | SO on sewer network | SJ8282297894 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 28.97 | 16 | 16.75 | 4 (installed 2019) | 100 | [5 empty] | UUG1423
United Utilities | WATER ST/NEW QUAY ST CSO | Water Street/New Quay Street CSO | 016993831 | MAN0172 | SO | SO on sewer network | SJ8312098220 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | THE RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 17.6 | 22 | 10.25 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1424
United Utilities | BRIDGE ST WEST CSO (281F9) | Bridge Street West CSO | 016993550 | MAN0174 | SO | SO on sewer network | SJ8332098360 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | THE RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 3.2 | 11 | 6 | 3 (installed 2020) | 100 | [5 empty] | UUG1425
United Utilities | CHORLTON STREET CSO 281J2 | CHORLTON STREET CSO | 01MAN0162 | MAN0162 | SO | SO on sewer network | SJ8451097820 | GB112069061152 | Medlock (Lumb Brook to Irwell) | SHOOTERS BROOK TRIB RVR MEDLOC | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.1 | 1 | 19.8 | 5 (installed 2018) | 100 | [5 empty] | UUG1426
United Utilities | FIRST AVENUE CSO | First Avenue CSO | 016993654 | MAN0178 | SO | SO on sewer network | SJ7975097470 | GB112069061161 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mersey) | PLUMPTON CLOUGH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.18 | 1 | 3 | 4 (installed 2019) | 99.83 | [5 empty] | UUG1427
United Utilities | EGERTON ST WORSLEY ST CSO | Egerton Street / Worsley Street CSO | 016983277 | MAN0181 | SO | SO on sewer network | SJ8279197530 | GB112069061152 | Medlock (Lumb Brook to Irwell) | THE RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 36.47 | 62 | 78 | 5 (installed 2018) | 96.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1428
United Utilities | HUNTS BANK COMBINED SEWER OVERFLOW | HUNTS BANK CSO | 01MAN0176 | MAN0176 | SO | SO on sewer network | SJ8897098920 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.07 | 1 | 0.25 | 4 (installed 2019) | 100 | [5 empty] | UUG1429
United Utilities | MOUNT STREET/GREEK STREET CSO | MOUNT STREET / GREEK STREET CSO | 01MAN0187 | MAN0187 | SO | SO on sewer network | SJ8453097390 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.2 | 1 | 6 | 4 (installed 2019) | 100 | [5 empty] | UUG1430
United Utilities | OXFORD ROAD/GROSVENOR STREET CSO | OXFORD ROAD / GROSVENOR STREET CSO | 01MAN0189 | MAN0189 | SO | SO on sewer network | SJ8415097461 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 28.1 | 28 | 34.75 | 4 (installed 2019) | 100 | [5 empty] | UUG1431
United Utilities | GORTON ROAD (LIGHTING TOWER) | Gorton Road CSO | NPSWQD010710 | MAN0199 | SO | SO on sewer network | SJ8604097020 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | BLACK BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 205.68 | 18 | 16.75 | 4 (installed 2019) | 99.98 | [5 empty] | UUG1432
United Utilities | HARTSHEAD CLOSE/MANSHAW ROAD CSO | HARTSHEAD CLOSE / MANSHAW ROAD CSO | 01MAN0203 | MAN0203 | SO | SO on sewer network | SJ9013897264 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | CULVERTED SECTION MOSS BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.37 | 2 | 4.75 | 4 (installed 2019) | 100 | [5 empty] | UUG1433
United Utilities | VAUGHAN STREET CSO | Vaughan Street Combined Sewer Overflow | 016993693 | MAN0218 | SO | SO on sewer network | SJ8688097060 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | CORN BROOK IN CULVERT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.77 | 2 | 1.75 | 4 (installed 2019) | 99.92 | [5 empty] | UUG1434
United Utilities | ALTRINCHAM RD WESTEND AVE CSO 431BS | ALTRINCHAM ROAD / WEST END AVENUE CSO | 01MAN0226 | MAN0226 | SO | SO on sewer network | SJ8431088730 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | GATLEY BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 1.73 | 13 | 14 | 6 (installed 2017) | 99.99 | [5 empty] | UUG1435
United Utilities | EDGE LANE/WILBRAHAM CSO | Edge Lane/Wilbraham Road CSO | 016993694 | MAN0228 | SO | SO on sewer network | SJ8078093260 | GB112069061040 | Chorlton Brook (Princess Parkway to Mersey) | CHORLTON BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 70.4 | 43 | 47.5 | 4 (installed 2019) | 100 |  |  | Data collection - EDM non-representative location | Scheduled | Other investigation - non-WINEP/Green Recovery | UUG1436
United Utilities | MAULDETH ROAD CSO | Mauldeth Road CSO | 016993515 | MAN0229 | SO | SO on sewer network | SJ8302093530 | GB112069061040 | Chorlton Brook (Princess Parkway to Mersey) | CHORLTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 32.93 | 19 | 22 | 4 (installed 2019) | 99.78 | [5 empty] | UUG1437
United Utilities | MAULDETH ROAD WEST CSO (28043) | Mauldeth Road West CSO | 01MAN0230 | MAN0230 | SO | SO on sewer network | SJ8340093650 | GB112069061040 | Chorlton Brook (Princess Parkway to Mersey) | CHORLTON BROOK VIA CULVERT | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 152.71 | 71 | 50.6667 | 3 (installed 2020) | 89.82 | Sensor failure / issue | Resolved - Apr | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1438
United Utilities | CHARLES STREET CSO | Charles Street CSO | 01MAN0183 | MAN0183 | SO | SO on sewer network | SJ8432097500 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 1.8 | 5 (installed 2018) | 96.21 | [5 empty] | UUG1439
United Utilities | BERESFORD ROAD CSO | Beresford Road Combined Sewer Overflow | 016942057 | MAN0234 | SO | SO on sewer network | SJ8655095240 | GB112069061060 | Platt Brook (Source to Fallowfield Bk) | CLVRT SECTION OF GORE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2.27 | 3 | 8.25 | 4 (installed 2019) | 96.76 | [5 empty] | UUG1440
United Utilities | ST WERBURGHS RD CSO SITE 282T5 | St Werbughes Road / Sandy Lane CSO | 01MAN0232 | MAN0232 | SO | SO on sewer network | SJ8234093340 | GB112069061040 | Chorlton Brook (Princess Parkway to Mersey) | CHORLTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0.25 | 4 (installed 2019) | 94.18 | [5 empty] | UUG1441
United Utilities | BURTON ROAD WITHINGTON CSO 28056 | Burton Road (Withington) CSO | 01MAN0237 | MAN0237 | SO | SO on sewer network | SJ8346091621 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 28.83 | 3 | 2.6667 | 6 (installed 2017) | 99.93 | [5 empty] | UUG1442
United Utilities | BARLOW MOOR RD/PALATINE RD CSO | Barlow Moor Road/Palatine Road CSO | 01MAN0236 | MAN0236 | SO | SO on sewer network | SJ8346091620 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Dec 2023 | 64.73 | 21 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1443
United Utilities | BIRCH HALL LN THORESWAY RD CSO | Birch Hall Lane/Thoresway Road CSO | 01MAN0245 | MAN0245 | SO | SO on sewer network | SJ8633095170 | GB112069061060 | Platt Brook (Source to Fallowfield Bk) | GORE BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.2 | 1 | 2 | 3 (installed 2020) | 100 | [5 empty] | UUG1444
United Utilities | MOUNT ROAD COMBINED SEWER OVERFLOW | Mount Road CSO | 01MAN0246 | MAN0246 | SO | SO on sewer network | SJ8807095271 | GB112069061060 | Platt Brook (Source to Fallowfield Bk) | GORE BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 7.67 | 11 | 10 | 4 (installed 2019) | 92.44 | [5 empty] | UUG1445
United Utilities | WITHINGTON PUMPING STATION 28009 | Withington PS | 01MAN0250 | MAN0250 | SO | Storm discharge at pumping station | SJ8091092840 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 492.34 | 127 | 116.1667 | 6 (installed 2017) | 99.94 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1446
United Utilities | BARLOW MOOR ROAD | Barlow Moor Road / Rowsley Avenue CSO | 01MAN0244 | MAN0244 | SO | SO on sewer network | SJ8329091780 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 782.93 | 111 | 18.5 | 6 (installed 2017) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1447
United Utilities | GREAT BRIDGEWATER ST CSO (281WI) | Great Bridgewater Street CSO | 016982707 | MAN0252 | SO | SO on sewer network | SJ8381097460 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0.33333 | 3 (installed 2020) | 100 | [5 empty] | UUG1448
United Utilities | BURTON ST NR DALTON ST CSO 281HX | Burton Street near Dalton Street CSO | 016982622 | MAN0263 | SO | SO on sewer network | SJ8486099630 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.33 | 2 | 12 | 5 (installed 2018) | 99.93 | [5 empty] | UUG1449
United Utilities | BESWICK ST ASHTON NEW RD CSO 281D0 | Beswick Street/Ashton New Road CSO | 016982710 | MAN0256 | SO | SO on sewer network | SJ8597098460 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 5 (installed 2018) | 100 | [5 empty] | UUG1450
United Utilities | MILL BROW/BLACKLEY NEW ROAD CSO | Mill Brow/Blackley New Road CSO | 016982717 | MAN0269 | SO | SO on sewer network | SD8520502856 | GB112069061131 | Irk (Wince to Irwell) | CULVERTED TRIB OF RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 6.2 | 21 | 17.75 | 4 (installed 2019) | 100 | [5 empty] | UUG1451
United Utilities | CHESTER ROAD/GREAT JACKSON ROAD CSO | Chester Road/Great Jackson Road CSO | 016982719 | MAN0276 | SO | SO on sewer network | SJ8336097430 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 36.14 | 15 | 12.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG1452
United Utilities | VERDON STREET/SCOTLAND CSO | Verdon Street/Scotland Combined Sewer Overflow | 016982715 | MAN0265 | SO | SO on sewer network | SJ8412099170 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.73 | 3 | 1.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1453
United Utilities | CAMBRIDGE STREET CSO 282D9 | Cambridge Street CSO | 016982721 | MAN0285 | SO | SO on sewer network | SJ8385097410 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0.2 | 5 (installed 2018) | 100 | [5 empty] | UUG1454
United Utilities | 161 A DICKENSON ROAD CSO | 161a Dickenson Road CSO | 016982725 | MAN0297 | SO | SO on sewer network | SJ8611095130 | GB112069061060 | Platt Brook (Source to Fallowfield Bk) | GORE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 2 | 4 (installed 2019) | 87.88 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1455
United Utilities | MAD HATTER PUB | The Mad Hatter Pub CSO | 016982724 | MAN0290 | SO | SO on sewer network | SJ8725095540 | GB112069061060 | Platt Brook (Source to Fallowfield Bk) | GORE BROOK | N/A | N/A | Not Applicable | Dec 2023 | 2787.07 | 150 |  | <1 yr (installed 2023) | 86.2745 | Installation set-up/design issue | N/A - Ongoing investigation | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1456
United Utilities | HILLKIRK STREET CSO (282I9) | Hillkirk Street CSO | 016982726 | MAN0298 | SO | SO on sewer network | SJ8615098500 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.43 | 1 | 0.33333 | 3 (installed 2020) | 99.99 | [5 empty] | UUG1457
United Utilities | FAIRFIELD STREET CSO | Fairfield Street CSO | 016982730 | MAN0309 | SO | SO on sewer network | SJ8543097630 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 14.3 | 15 | 21 | 4 (installed 2019) | 84.11 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1458
United Utilities | BROMLEY STREET CSO 281MT | Bromley Street Nr Railway Arch CSO | 016982627 | MAN0310 | SO | SO on sewer network | SJ8449099400 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.83 | 6 | 18.2 | 5 (installed 2018) | 95.92 | [5 empty] | UUG1459
United Utilities | 3 WOOD RD | 3 Wood Road CSO | 01MAN0311 | MAN0311 | SO | SO on sewer network | SJ8235095200 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | OUEL BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0.4 | 5 (installed 2018) | 97.09 | [5 empty] | UUG1460
United Utilities | EDGE LANE/MANCHESTER ROAD/HIGH LANE | Edge Lane/Manchester Road/High Lane | 016982629 | MAN0315 | SO | SO on sewer network | SJ8093693606 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | TRIB CHORLETON BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.17 | 5 | 4.25 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1461
United Utilities | CULCETH LANE CSO | Culcheth Lane CSO | 016982731 | MAN0313 | SO | SO on sewer network | SJ8840099430 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0.75 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1462
United Utilities | MILL STREET BRADFORD MANCHESTER CSO | Mill Street CSO | 016982733 | MAN0320 | SO | SO on sewer network | SJ7066055300 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.23 | 1 | 1.2 | 5 (installed 2018) | 100 | [5 empty] | UUG1463
United Utilities | JUNCTION OF ASHTON NEW ROAD CSO | Junction of Ashton New Road CSO | 016982734 | MAN0323 | SO | SO on sewer network | SJ8732097120 | GB112069061210 | Hardshaw (Windle) Brook | WINDLE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0.25 | 4 (installed 2019) | 100 | [5 empty] | UUG1464
United Utilities | BRISCOE LANE CSO | Briscoe Lane CSO | 016982735 | MAN0337 | SO | SO on sewer network | SJ8747099340 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 85.51 | 24 | 14.75 | 4 (installed 2019) | 99.14 | [5 empty] | UUG1465
United Utilities | MALLARD STREET/CHARLES STREET CSO | Mallard Street/Charles Street CSO | 016982736 | MAN0343 | SO | SO on sewer network | SJ8417197501 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 42.25 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1466
United Utilities | BEECH ROAD/CLAUDE RAOD CSO | Beech Road/Claude Road CSO | 016993509 | MAN0325 | SO | SO on sewer network | SJ8192093240 | GB112069061040 | Chorlton Brook (Princess Parkway to Mersey) | CHORLTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.53 | 6 | 5 | 4 (installed 2019) | 97.72 | [5 empty] | UUG1467
United Utilities | CLARE RD/DAVENHILL RD CSO | Clare Road/Davenhill Road CSO | 016940833 | MAN0345 | SO | SO on sewer network | SJ8735093540 | GB112069061410 | Fallowfield Brook | CRINGLE BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 3 | 4 (installed 2019) | 100 | [5 empty] | UUG1468
United Utilities | LOMBARD GR/LORNE RD | Lombard Grove/Lorne Road CSO | 016982821 | MAN0344 | SO | SO on sewer network | SJ8523093520 | GB112069061410 | Fallowfield Brook | CRINGLE BROOK | N/A | N/A | Not Applicable | Dec 2023 | 0.33 | 4 |  | <1 yr (installed 2023) | 98.1928 | [5 empty] | UUG1469
United Utilities | SOUTH OF BLACKLEY NEW ROAD CSO | South Blackley New Road CSO | 016982986 | MAN0347 | SO | SO on sewer network | SD8390003150 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.37 | 2 | 1 | 4 (installed 2019) | 93.79 | [5 empty] | UUG1470
United Utilities | DANTZIC STREET CSO | Dantzic Street CSO | 016982951 | MAN0348 | SO | SO on sewer network | SJ8465099560 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.57 | 3 | 2.8 | 5 (installed 2018) | 100 | [5 empty] | UUG1471
United Utilities | KENYON LANE CSO | Kenyon Lane CSO | 016982953 | MAN0352 | SO | SO on sewer network | SD8770001160 | GB112069061131 | Irk (Wince to Irwell) | TRIB RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 486.94 | 95 | 50.25 | 4 (installed 2019) | 97.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1472
United Utilities | PRINCESS ST/WHITWORTH ST CSO 282MN | Princess Street/Whitworth Street CSO | 016982950 | MAN0354 | SO | SO on sewer network | SJ8433097521 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 13.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG1473
United Utilities | BURY NEW ROAD/WATERLOO ROAD CSO | Bury New Road/Waterloo Road CSO | 016982984 | MAN0360 | SO | SO on sewer network | SJ8349099550 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 328.1 | 17 | 33 | 4 (installed 2019) | 72.59 | Comms failure / issue | Resolved - January after reporting year |  |  | Other investigation - non-WINEP/Green Recovery | UUG1474
United Utilities | STRETFORD RD/UPPER MOSS LN JUNC CSO | Stretford Road and Upper Moss Lane Junction CSO | 01MAN0365 | MAN0365 | SO | SO on sewer network | SJ8252097362 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 8.57 | 7 | 5.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG1475
United Utilities | CITY RD CSO 288OV | City Road CSO | 016982954 | MAN0366 | SO | SO on sewer network | SJ8252097360 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | VIA SWS MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 20.4 | 10 | 12.2 | 5 (installed 2018) | 100 | [5 empty] | UUG1476
United Utilities | ROLLS CRESCENT/YEW STREET CSO | Rolls Crescent/Yew Street CSO | 016982958 | MAN0367 | SO | SO on sewer network | SJ8252097363 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 38.17 | 17 | 17.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG1477
United Utilities | VAUGHAN STREET CSO | Bennett Street CSO | 016982957 | MAN0376 | SO | SO on sewer network | SJ8688097060 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | CLVRT SECTION OF CORN BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 13.2 | 5 (installed 2018) | 71.94 | Installation set-up/design issue | Resolved - Nov |  |  |  | UUG1478
United Utilities | QUEENS ROAD/SCORPTON STREET CSO | Queens Road/Scorpton Street CSO | 016982952 | MAN0351 | SO | SO on sewer network | SD8574000500 | GB112069061131 | Irk (Wince to Irwell) | CULVERTED SECTION MOSTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.43 | 3 | 2.5 | 4 (installed 2019) | 95.17 | [5 empty] | UUG1479
United Utilities | WILMSLOW RD/BROOK RD CSO | Wilmslow Road/Brook road CSO | 016982985 | MAN0378 | SO | SO on sewer network | SJ8534093480 | GB112069061410 | Fallowfield Brook | LEIGH BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1480
United Utilities | KENWORTHY LANE PS | Kenworthy Lane PS | 016982983 | MAN0385 | SO | Storm discharge at pumping station | SJ8254091080 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1481
United Utilities | SLEDMOOR ROAD CSO | Sledmoor Road CSO | 016982979 | MAN0387 | SO | SO on sewer network | SJ8141091950 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Dec 2023 | 7.77 | 24 |  | <1 yr (installed 2023) | 99.45 | [5 empty] | UUG1482
United Utilities | NORTHUMBERLAND RD/STRETFORD RD CSO | Northumberland Street/Stretford Road CSO | 016982992 | MAN0388 | SO | SO on sewer network | SJ8170096650 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 3.07 | 4 | 158.3333 | 3 (installed 2020) | 58.35 | Comms failure / issue | Resolved - January after reporting year | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1483
United Utilities | BRIDGE STREET CSO | Bridge Street CSO | 016982898 | MAN0392 | SO | SO on sewer network | SJ8333098360 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.77 | 4 | 8.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1484
United Utilities | BURY NEW RD LOCKETT ST CSO | Bury New Road/Lockett Street CSO | 016982899 | MAN0393 | SO | SO on sewer network | SJ8346099320 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL VIA SRF WTR SEWER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 4.7 | 7 | 13.2 | 5 (installed 2018) | 100 | [5 empty] | UUG1485
United Utilities | WATER STREET CSO (284TV) | Water Street (Manchester) CSO | 016982993 | MAN0391 | SO | SO on sewer network | SJ8295098030 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | RIVER IRWELL | N/A | N/A | Not Applicable | Dec 2023 | 1.73 | 9 |  | <1 yr (installed 2023) | 99.98 | [5 empty] | UUG1486
United Utilities | MANCUNIAN WAY CSO | Mancunian Way CSO | 016982729 | MAN0399 | SO | SO on sewer network | SJ8494097510 | GB112069061152 | Medlock (Lumb Brook to Irwell) | RIVER MEDLOCK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 6.65 | 10 | 14 | 3 (installed 2020) | 100 | [5 empty] | UUG1487
United Utilities | CHESTER STREET CSO | Chester Street CSO | 016983278 | MAN0400 | SO | SO on sewer network | SJ8408097350 | GB112069061152 | Medlock (Lumb Brook to Irwell) | THE RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.14 | 1 | 2.8 | 5 (installed 2018) | 100 | [5 empty] | UUG1488
United Utilities | KENDALL ROAD BLACKLEY CSO | Kendall Road (Blackley) Combined Sewer Overflow | 016982987 | MAN0398 | SO | SO on sewer network | SD8383003360 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK VIA BIRCH BROOK CLVR | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 4.03 | 16 | 4.25 | 4 (installed 2019) | 100 | [5 empty] | UUG1489
United Utilities | PALMERSTON STREET CSO | Palmerston Street CSO | 016983280 | MAN0402 | SO | SO on sewer network | SJ8589097990 | GB112069060660 | Harrop Brook | THE RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1490
United Utilities | PALMERSTON STREET CSO | Palmerston Street CSO | 016983280 | MAN0401 | SO | SO on sewer network | SJ8589097990 | GB112069061152 | Medlock (Lumb Brook to Irwell) | THE RIVER MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.07 | 1 | 2 | 4 (installed 2019) | 100 | [5 empty] | UUG1492
United Utilities | MANCHESTER OLD ROAD CSO | Manchester Old Road CSO | 016982916 | ROC0009 | SO | SO on sewer network | SD8444004740 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2.37 | 8 | 4.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1493
United Utilities | JOHN LEE FOLD CSO | John Lee Fold CSO | 016982900 | ROC0012 | SO | SO on sewer network | SD8737006200 | GB112069061161 | Irk (Sourtce to Wince Brook) | WHIT BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.27 | 1 | 4 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1494
United Utilities | BOARSHAW ROAD CSO | BOARSHAW ROAD CSO | 01ROC0013 | ROC0013 | SO | SO on sewer network | SD8759006660 | GB112069061161 | Irk (Sourtce to Wince Brook) | WHIT BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 39.13 | 55 | 66.5 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1495
United Utilities | WAVERLEY RD CSO 352W4 | Waverley Road CSO | 01ROC0014 | ROC0014 | SO | SO on sewer network | SD8764007330 | GB112069061161 | Irk (Sourtce to Wince Brook) | TRUB BROOK RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 59.17 | 61 | 117.8333 | 6 (installed 2017) | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1496
United Utilities | MAINWAYEAST/LINCOLN ROAD CSO | Mainway/Lincoln Road Combined Sewer Overflow | 01ROC0015 | ROC0015 | SO | SO on sewer network | SD8810004590 | GB112069061120 | Wince Brook | WINCE BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 4.43 | 15 | 10.75 | 4 (installed 2019) | 99.98 | [5 empty] | UUG1497
United Utilities | MANCHESTER NEW ROAD CSO | Manchester New Road Combined Sewer Overflow | 016993577 | ROC0016 | SO | SO on sewer network | SD8649004482 | GB112069061131 | Irk (Wince to Irwell) | BOARDMAN BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2.7 | 9 | 11 | 4 (installed 2019) | 100 | [5 empty] | UUG1498
United Utilities | MAINWAY/WORCESTER ROAD CSO | Mainway/Worcester Road CSO | 016993575 | ROC0017 | SO | SO on sewer network | SD8649004481 | GB112069061131 | Irk (Wince to Irwell) | BOARDMAN BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 121 | 42 | 31.5 | 4 (installed 2019) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1499
United Utilities | BOOTHROYDEN ROAD CSO | Boothroyden Road CSO | 016993590 | ROC0018 | SO | SO on sewer network | SD8498004970 | GB112069061131 | Irk (Wince to Irwell) | THE RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 558.59 | 124 | 106.25 | 4 (installed 2019) | 99.88 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1500
United Utilities | WHITLEY DRIVE CSO | Whiteley Drive CSO | 016993576 | ROC0116 | SO | SO on sewer network | SD8807005120 | GB112069061120 | Wince Brook | WINCE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 200.89 | 74 | 56.75 | 4 (installed 2019) | 99.92 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1501
United Utilities | LONG STREET COMBINED SEWER OVERFLOW | Long Street CSO (near the Market Place) | 016993581 | ROC0124 | SO | SO on sewer network | SD8704006010 | GB112069061161 | Irk (Sourtce to Wince Brook) | CLVRT'D SECTION THE RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.37 | 3 | 4.25 | 4 (installed 2019) | 100 | [5 empty] | UUG1502
United Utilities | TINTERN ROAD (OFF THE LAND) CSO | Tintern Road (Off the Land) CSO | EPRQB3594AD | ROC0134 | SO | SO on sewer network | SD8733007390 | GB112069061161 | Irk (Sourtce to Wince Brook) | TRIB OF TRUB BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.17 | 2 | 8.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1503
United Utilities | KIRKWAY COMBINED SEWER OVERFLOW | Kirkway CSO | 016950343 | ROC0136 | SO | SO on sewer network | SD8724005591 | GB112069061120 | Wince Brook | WINCE BROOK, TRIB OF RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 177.39 | 80 | 68.25 | 4 (installed 2019) | 99.07 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1504
United Utilities | BOARDSHAW ROAD CSO | Boardshaw Road CSO | 016950217 | ROC0141 | SO | SO on sewer network | SD8752006470 | GB112069061161 | Irk (Sourtce to Wince Brook) | WHIT BROOK, TRIB OF RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 3.25 | 4 (installed 2019) | 99.94 | [5 empty] | UUG1505
United Utilities | SPRING VALE COMBINED SEWER OVERFLOW | Spring Vale CSO | 016982642 | ROC0166 | SO | SO on sewer network | SD8753006030 | GB112069061161 | Irk (Sourtce to Wince Brook) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 4.77 | 9 | 6.75 | 4 (installed 2019) | 99.57 | [5 empty] | UUG1506
United Utilities | MIDDLETON MAIN OUTFALL | MIDDLETON MAIN OUTFALL CSO | 016982643 | ROC0167 | SO | SO on sewer network | SD8558005230 | GB112069061131 | Irk (Wince to Irwell) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 365.31 | 99 | 86.75 | 4 (installed 2019) | 98.04 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1507
United Utilities | WOOD STREET CSO | Wood Street CSO | 016982644 | ROC0168 | SO | SO on sewer network | SD8658006240 | GB112069061161 | Irk (Sourtce to Wince Brook) | RIVER IRK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 144.07 | 88 | 98.5 | 6 (installed 2017) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1508
United Utilities | MOSSWAY CSO | Mossway CSO | 016982901 | ROC0185 | SO | SO on sewer network | SD8686003920 | GB112069061131 | Irk (Wince to Irwell) | BOARDMAN BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1509
United Utilities | FIELDING STREET CSO (ROC0193) | Fielding Street CSO | EPRJB3892VC | ROC0193 | SO | SO on sewer network | SD8734506810 | GB112069061161 | Irk (Sourtce to Wince Brook) | CLV TRIB OF WHIT BROOK | N/A | N/A | Not Applicable | Dec 2023 | 405.93 | 133 |  | <1 yr (installed 2023) | 96.5278 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1510
United Utilities | BURY NEW ROAD SALFORD CSO | Ashworth Street CSO | 016993784 | SAL0024 | SO | SO on sewer network | SJ8308399365 | GB112069061451 | Irwell (Croal to Irk) | THE RIVER IRWELL VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 100.21 | 45 | 38 | 5 (installed 2018) | 86.81 | Installation set-up/design issue | N/A - Ongoing investigation | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1511
United Utilities | MOSS LANE ACRE LANE CSO 431AM | Moss Lane/Acre Lane CSO | 01STK0010 | STK0010 | SO | SO on sewer network | SJ8905084711 | GB112069060940 | Micker Brook | CARR BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2.7 | 4 | 7.8 | 5 (installed 2018) | 99.99 | [5 empty] | UUG1512
United Utilities | LANGDALE ROAD CSO 432KA | Langdale Road CSO | 01STK0015 | STK0015 | SO | SO on sewer network | SJ8905084710 | GB112069060940 | Micker Brook | CARR BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.27 | 1 | 20.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1513
United Utilities | LUMB LANE CSO (432D0) | Lumb Lane CSO | 01STK0016 | STK0016 | SO | SO on sewer network | SJ8921084610 | GB112069060940 | Micker Brook | CARR BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 8.5 | 17 | 12.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1514
United Utilities | BRAMHALL LN STH (NO 221) | Bramhall Lane South (No 221) | 01STK0017 | STK0017 | SO | SO on sewer network | SJ8934086480 | GB112069060940 | Micker Brook | Micker Brook | N/A | N/A | Not Applicable | Dec 2023 | 7.3 | 1 |  | <1 yr (installed 2023) | 98.8764 | [5 empty] | UUG1515
United Utilities | ABNEY HALL | Abney Hall CSO | 01STK0018 | STK0018 | SO | SO on sewer network | SJ8570089250 | GB112069060940 | Micker Brook | Micker Brook | N/A | N/A | Not Applicable | Dec 2023 | 4.8 | 11 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1516
United Utilities | 650YDS DS KINGWAY RVR BRIDGE CSO | 650 yards downstream of Kingsway River Bridge CSO | 01STK0019 | STK0019 | SO | SO on sewer network | SJ8450089370 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 1622.53 | 132 | 83.5 | 6 (installed 2017) | 89.48 | Comms failure / issue | Resolved - January after reporting year | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1517
United Utilities | BRAMHALL PARK CSO | Bramhall Park CSO | EPRQB3594WA | STK0027 | SO | SO on sewer network | SJ8648086790 | GB112069060940 | Micker Brook | LADY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 143.72 | 57 | 49 | 4 (installed 2019) | 90.38 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1518
United Utilities | BRAMHALL ISLAND CSO | Bramhall Island CSO | EPRQB3595AJ | STK0033 | SO | SO on sewer network | SJ8926086360 | GB112069060940 | Micker Brook | Lady Brook | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 4.3 | 15 | 16 | 4 (installed 2019) | 100 | [5 empty] | UUG1519
United Utilities | OUTSIDE 91 STYAL ROAD CSO | Outside 91 Styal Road CSO | 01STK0048 | STK0048 | SO | SO on sewer network | SJ8397087670 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | GATLEY BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 85.57 | 39 | 36 | 3 (installed 2020) | 100 | [5 empty] | UUG1520
United Utilities | CHEADLE GOLF COURSE CSO (43198) | Cheadle Golf Course CSO | 016940447 | STK0049 | SO | SO on sewer network | SJ8623087880 | GB112069060940 | Micker Brook | MICKER BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 125.73 | 50 | 53.3333 | 3 (installed 2020) | 72.65 | Sensor failure / issue | Resolved - Jul | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1521
United Utilities | CARR WOOD COMBINED SEWER OVERFLOW | Carr Wood CSO | 016982756 | STK0051 | SO | SO on sewer network | SJ8898085860 | GB112069060940 | Micker Brook | CARR BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 403.6 | 100 | 91.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1522
United Utilities | BILLY'S LANE CSO | Billy's Lane CSO | 016982767 | STK0121 | SO | SO on sewer network | SJ8703086160 | GB112069060940 | Micker Brook | TURVES BROOK,TRIB MICKER BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1109.01 | 81 | 50.6667 | 3 (installed 2020) | 79.63 | Sensor failure / issue | Resolved - Aug | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1523
United Utilities | 59D TURVES ROAD CSO 432VY | No. 59d Turves Road CSO | 016982768 | STK0122 | SO | SO on sewer network | SJ8684086520 | GB112069060940 | Micker Brook | TURVES BROOK, TRIB MICKER BRK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2.4 | 4 | 8 | 5 (installed 2018) | 97.44 | [5 empty] | UUG1524
United Utilities | BRIARLANDS CL CSO AKA 4 ACK LANE | Briarlands Close CSO (formerly known as Rear of 40 Ack Lane CSO) | 016982769 | STK0123 | SO | SO on sewer network | SJ8907084740 | GB112069060940 | Micker Brook | CARRWOOD PK BROOK TRIB LADY B | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 717.1 | 120 | 73.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1525
United Utilities | 50 BRIDGE LANE BRAMHALL CSO | 50 Bridge Lane CSO | 016982681 | STK0125 | SO | SO on sewer network | SJ8973086300 | GB112069060940 | Micker Brook | LADY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.57 | 3 | 6 | 5 (installed 2018) | 100 | [5 empty] | UUG1526
United Utilities | MILL LANE CEMETERY CSO | Mill Lane Cemetery CSO | 01STK0128 | STK0128 | SO | SO on sewer network | SJ8585089200 | GB112069060940 | Micker Brook | CHORLTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 17.63 | 18 | 13.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1527
United Utilities | 258 COUNCILLOR LANE | 258 Councillor Lane CSO | 016982684 | STK0129 | SO | SO on sewer network | SJ8727087710 | GB112069060940 | Micker Brook | MICKER BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 6.93 | 19 | 19.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1528
United Utilities | MOORFILED HALL CSO 432G4 | Moorfield Hall CSO | 016982981 | STK0141 | SO | SO on sewer network | SJ8845083800 | GB112069061360 | Dean (Bollington to Bollin) | TRIB SPATH BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 204.07 | 64 | 38.5 | 6 (installed 2017) | 99.99 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1529
United Utilities | HALL MOSS LANE PS | Hall Moss Lane PS | 016992842 | STK0144 | SO | Storm discharge at pumping station | SJ8801083850 | GB112069061360 | Dean (Bollington to Bollin) | SPATH BROOK | N/A | N/A | Not Applicable | Dec 2023 | 0.11 | 1 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1530
United Utilities | CLAYTON BRIDGE | Clayton Bridge CSO | 01TAM0004 | TAM0004 | SO | SO on sewer network | SJ8909099420 | GB112069061152 | Medlock (Lumb Brook to Irwell) | River Medlock | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 662.7 | 99 | 70 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1531
United Utilities | MEDLOCK SPORTS CENTRE CSO | Medlock Sports Centre CSO | 016983275 | TAM0005 | SO | SO on sewer network | SJ9049199291 | GB112069061151 | Medlock (Source to Lumb Brook) | LUMB BROOK VIA SURFACE WTR SEW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 8.86 | 11 | 10.4 | 5 (installed 2018) | 99.97 | [5 empty] | UUG1532
United Utilities | CHAPPELL ROAD CSO | Chappell Road CSO | 016983267 | TAM0006 | SO | SO on sewer network | SJ9045799436 | GB112069061151 | Medlock (Source to Lumb Brook) | LUMB BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 142.83 | 75 | 64 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1533
United Utilities | URMSTON SSO | Richmond Road CSO | 016941193 | TRA0003 | SO | SO on sewer network | SJ7786097992 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Dec 2023 | 713.1 | 104 |  | <1 yr (installed 2023) | 96.4706 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1534
United Utilities | WOODHOUSE ROAD CSO 459BC | Woodhouse Road CSO | 016993438 | TRA0005 | SO | SO on sewer network | SJ7534095800 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | LONGFORD BRK BENT LANES BRK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 292.9 | 76 | 93.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1535
United Utilities | CECIL ROAD/ASHLEY ROAD CSO | Cecil Road/Ashley Road CSO | 01TRA0012 | TRA0012 | SO | SO on sewer network | SJ7682085960 | GB112069061382 | Bollin (Ashley Mill to Manchester Ship Canal) | TRIB OF RIVER BOLLIN VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 100 | [5 empty] | UUG1536
United Utilities | HAWTHORN ROAD CSO 451YJ | Hawthorn Road CSO | 01TRA0013 | TRA0013 | SO | SO on sewer network | SJ7748087990 | GB112069061260 | Timperley Brook | TIMPERLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 4.2 | 5 (installed 2018) | 99.52 | [5 empty] | UUG1537
United Utilities | CHAPEL LANE | Chapel Lane CSO | 01TRA0016 | TRA0016 | SO | SO on sewer network | SJ7919085550 | GB112069061381 | Bollin (River Dean to Ashley Mill) | RIVER BOLLIN | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1538
United Utilities | GOLF ROAD PUMPING STATION | Golf Road PS | 016892329 | TRA0045 | SO | Storm discharge at pumping station | SJ7778087790 | GB112069061260 | Timperley Brook | TIMPERLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 131.22 | 73 | 60 | 5 (installed 2018) | 84.61 | Capital / maintenance works affect EDM operation | Resolved - Nov | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1539
United Utilities | BARROW LANE CSO (451G7) | Barrow Lane CSO | 01TRA0059 | TRA0059 | SO | SO on sewer network | SJ7840085170 | GB112069061381 | Bollin (River Dean to Ashley Mill) | TRIB OF RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 91.97 | 72 | 56.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1540
United Utilities | TRAFFORD PARK ROAD CSO | Trafford Park Road CSO | 016940329 | TRA0070 | SO | SO on sewer network | SJ7977097430 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 9.8 | 7 | 7 | 3 (installed 2020) | 100 | [5 empty] | UUG1541
United Utilities | LOSTOCK ROAD CSO | Lostock Road CSO | NPSWQD010711 | TRA0074 | SO | SO on sewer network | SJ7707095780 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | BENT LANES BROOK VIA SW SEWER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 167.17 | 81 | 68.5 | 4 (installed 2019) | 92.32 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1542
United Utilities | PARK ROAD ARTHOG ROAD CSO 452LS | Park Road/Arthog Road CSO | 01TRA0078 | TRA0078 | SO | SO on sewer network | SJ7752085720 | GB112069061381 | Bollin (River Dean to Ashley Mill) | RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 574.27 | 141 | 142 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1543
United Utilities | ASHBURTON RD/CENTRAL PARK CSO | Ashburton Road/Central Park CSO | 016982253 | TRA0080 | SO | SO on sewer network | SJ7886696785 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.77 | 4 | 9.25 | 4 (installed 2019) | 100 | [5 empty] | UUG1544
United Utilities | DUMPLINGTON CIRCLE | Dumplington Circle CSO | 016982695 | TRA0085 | SO | SO on sewer network | SJ7667097560 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Dec 2023 | 28.33 | 5 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1545
United Utilities | HALE STORM TANKS & PUMPING STATION | Hale Storm Tanks and WwPPS | 016940005 | TRA0102 | SO | Storm discharge at pumping station | SJ7729085590 | GB112069061381 | Bollin (River Dean to Ashley Mill) | RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 21.2 | 10 | 50.3333 | 3 (installed 2020) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP or Green Recovery | UUG1546
United Utilities | HALE STORM TANKS & PUMPING STATION | Hale Storm Tanks and WwPPS | 016940005 | TRA0102 | ST | Storm discharge at pumping station | SJ7729085590 | GB112069061381 | Bollin (River Dean to Ashley Mill) | RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 2231.29 | 120 | 40 | 3 (installed 2020) | 90.01 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1547
United Utilities | CLARENCE STREET CSO | Clarence Street CSO | 017190797 | BBN0101 | SO | SO on sewer network | SD6871023540 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 137.16 | 62 | 69.5 | 4 (installed 2019) | 58.82 | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1548
United Utilities | BOLTON ROAD CSO | Bolton Road CSO | 01BBN0105 | BBN0105 | SO | SO on sewer network | SD6952021260 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | UNNAMED TRIB OF RIVER DARWEN | N/A | N/A | Not Applicable | Dec 2023 | 29.25 | 20 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1549
United Utilities | GRIMSHAW STREET CSO | Grimshaw Street Combined Sewer Overflow (Site ID 05033) (BBN0107) | 017190805 | BBN0107 | SO | SO on sewer network | SD6978021120 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 97.56 | 43 | 36.5 | 4 (installed 2019) | 99.24 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1550
United Utilities | COTTON HALL STREET CSO | COTTON HALL STREET CSO | 01BBN0117 | BBN0117 | SO | SO on sewer network | SD6925022850 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIBUTARY OF RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 44.2 | 66 | 59.3333 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1551
United Utilities | HIGHER PERRY ST/BLACK LAUREL ST CSO | HIGHER PERRY STREET/BACK LAUREL CSO | 01BBN0118 | BBN0118 | SO | SO on sewer network | SD6964022710 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIBUTARY OF RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 118.4 | 97 | 99 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1552
United Utilities | ANYON STREET/LAUREL AVE CSO | ANYON STREET / LAUREL AVENUE CSO | 01BBN0119 | BBN0119 | SO | SO on sewer network | SD6985022750 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIBUTARY OF RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 38.83 | 58 | 90.25 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1553
United Utilities | FOOTPATH NR CROSS ST CSO | Footpath Near Cross Street CSO | 017190822 | BBN0106 | SO | SO on sewer network | SD6975021230 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 1.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1554
United Utilities | RAILWAY ROAD/SOUTH STREET CSO | RAILWAY ROAD / SOUTH STREET CSO | 01BBN0121 | BBN0121 | SO | SO on sewer network | SD6928022300 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | CLVRTD SECTION OF RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 3.5 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1555
United Utilities | CHURCH STREET/PARLIAMENT STREET CSO | CHURCH STREET / PARLIAMENT STREEET CSO | 01BBN0122 | BBN0122 | SO | SO on sewer network | SD6928022180 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | CULVERTED SECTION RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.83 | 5 | 8.75 | 4 (installed 2019) | 97 | [5 empty] | UUG1556
United Utilities | REDEARTH ROAD/SUDELL ROAD CSO | REDEARTH ROAD / SUDELL ROAD CSO | 01BBN0124 | BBN0124 | SO | SO on sewer network | SD6935022090 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.1 | 1 | 15.3333 | 3 (installed 2020) | 96.82 | [5 empty] | UUG1557
United Utilities | BALLE STREET HILTON STREET CSO | BALLE STREET / HILTON STREET CSO | 01BBN0127 | BBN0127 | SO | SO on sewer network | SD6940021610 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 51.3 | 67 | 69.25 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1558
United Utilities | BALLE STREET HILTON STREET CSO | Balle Street CSO No.X | 01BBN0128 | BBN0128 | SO | SO on sewer network | SD6940021610 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 104.67 | 74 | 74 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1559
United Utilities | SUDELL ROAD CSO | Sudell Road CSO | 017180464 | BBN0136 | SO | SO on sewer network | SD6980022200 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIB RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 31.77 | 30 | 26.5 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1560
United Utilities | KAY STREET CSO | Kay Street | 017180465 | BBN0137 | SO | SO on sewer network | SD6957022310 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIB RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 3.2 | 18 | 26 | 4 (installed 2019) | 100 | [5 empty] | UUG1561
United Utilities | 28 TYTHEBARN ST | 28 Tythebarn Street CSO | 01BBN0120 | BBN0120 | SO | SO on sewer network | SD6957022320 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN (SEWER) | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 10.15 | 22 | 7.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG1562
United Utilities | SUDELLSIDE STREET | Sudellside Street CSO | 017180466 | BBN0138 | SO | SO on sewer network | SD6980022210 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIB RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0 | 4 (installed 2019) | 100 | [5 empty] | UUG1563
United Utilities | CRANBERRY LANE CSO | Cranberry Lane CSO | 017180469 | BBN0143 | SO | SO on sewer network | SD7021021080 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIB RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.73 | 3 | 6.75 | 4 (installed 2019) | 100 | [5 empty] | UUG1564
United Utilities | BOLTON ROAD CSO | Bolton Road CSO | 017180468 | BBN0142 | SO | SO on sewer network | SD6959021070 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIBUTARY OF RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 99.99 | [5 empty] | UUG1565
United Utilities | QUEENS ROAD (DARWEN) CSO | Queen's Road CSO | 017180470 | BBN0145 | SO | SO on sewer network | SD6966020510 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIBUTARY OF RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 100 | [5 empty] | UUG1566
United Utilities | VALE STREET | Vale Street | 017180471 | BBN0146 | SO | SO on sewer network | SD6884022540 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIB RIVER DARWEN | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1567
United Utilities | BELGRAVE ROAD CSO | Belgrave Road CSO | 017180472 | BBN0147 | SO | SO on sewer network | SD6890021810 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | TRIBUTARY OF RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 2 | 3 (installed 2020) | 100 | [5 empty] | UUG1568
United Utilities | WOODVALE FLATS CSO | Woodvale Flats combined sewer overflow (059AF) (BBN0151) | 017180476 | BBN0151 | SO | SO on sewer network | SD6888022570 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 7.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1569
United Utilities | HINDLE STREET CSO | Hindle Street CSO | 017190774 | BBN0162 | SO | SO on sewer network | SD6901022680 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | RIVER DARWEN VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 12.03 | 29 | 27.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG1570
United Utilities | BOLTON ROAD/ASTLEY STREET CSO | Bolton Road/ Astley Street CSO | 017190911 | BBN0164 | SO | SO on sewer network | SD6950021290 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | KEBBS BROOK,TRIB OF RIV DARWEN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 29.25 | 20 | 14 | 3 (installed 2020) | 99.7 | [5 empty] | UUG1571
United Utilities | Lower Eccleshill Road CSO | Lower Eccleshill Road CSO | 17160025 | BBN0169 | ST | SO on sewer network | SD6892524108 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | River Darwen | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 908.05 | 179 | 44.75 | 4 (installed 2019) | 99.86 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1572
United Utilities | DALSTON WWTW | DALSTON WwTW | 017670115 | 17670115 | ST | Storm tank at WwTW | NY3796051170 | GB102076073880 | Caldew d/s Caldbeck | RIVER CALDEW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 633.89 | 34 | 42.4 | 5 (installed 2018) | 62.27 | Sensor failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1573
United Utilities | DALSTON ROAD PS | Dalston Sewage PS, CSO | 017680318 | CAR0077 | SO | Storm discharge at pumping station | NY3861054060 | GB102076073880 | Caldew d/s Caldbeck | FAIRY BECK CULVERT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 39.8 | 25 | 20.4 | 5 (installed 2018) | 99.95 | [5 empty] | UUG1574
United Utilities | CULGAITH WWTW | CULGAITH WWTW | 17670167 | 17670167 | SO | Inlet SO at WwTW | NY6017629532 | GB102076070980 | Eden Lyvennet to Eamont | The River Eden | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1575
United Utilities | CULGAITH STW | CULGAITH WwTW | 017670167 | 17670167 | ST | Storm tank at WwTW | NY6010029500 | GB102076070980 | Eden Lyvennet to Eamont | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0 | 0 | 0 | 6 (installed 2017) | 100 | [5 empty] | UUG1576
United Utilities | CROSTON WWTW CRSTN | CROSTON WwTW | 017060017 | 17060017 | ST | Storm tank at WwTW | SD4797018660 | GB112070064861 | Yarrow Culbeck Brook to tidal | RIVER YARROW | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 703.21 | 89 | 73.1667 | 6 (installed 2017) | 93.59 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1577
United Utilities | COWLING FARM CSO | Cowling Farm CSO | 01CHR0007 | CHR0007 | SO | SO on sewer network | SD5577114819 | GB112070064952 | Yarrow DS Big Lodge Water | CLANCUTT BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1354.38 | 88 | 75.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1578
United Utilities | BEHIND 33 THE ORCHARD CSO 123KF | Behind 33 The Orchard CSO | 01CHR0008 | CHR0008 | SO | SO on sewer network | SD4910019080 | GB112070064912 | Lostock DS Farington Weir | TRIB OF RIVER LOSTOCK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 94.33 | 34 | 25.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1579
United Utilities | MAVIS DRIVE | Mavis Drive CSO | 01CHR0006 | CHR0006 | SO | SO on sewer network | SD5616014660 | GB112070064952 | Yarrow DS Big Lodge Water | CLANCUTT BROOK | N/A | N/A | Not Applicable | Commissioned pre-2016 - full year data expected | 1013.34 | 142 | 17.8 | 8 (installed 2015) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1580
United Utilities | HEWLETT AVENUE CSO | Hewlett Avenue CSO | NPSWQD010698 | CHR0011 | SO | SO on sewer network | SD5590014090 | GB112070064952 | Yarrow DS Big Lodge Water | TANYARD BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 49.86 | 41 | 39.75 | 4 (installed 2019) | 98.96 |  |  | Data collection - EDM non-representative location | Resolved - Dec |  | UUG1581
United Utilities | SOUTH PARK HALL/STOCKS LANE HESKIN | SOUTH PARK HALL / STOCKS LANE HESKIN CSO | TBC | CHR0012 | SO | SO on sewer network | SD5336015480 | GB112070064920 | Trib of Syd Brook | SYD BROOK | N/A | N/A | Not Applicable | Dec 2023 | 997.11 | 132 |  | <1 yr (installed 2023) | 100 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1582
United Utilities | Wood Lane Road, near High Barn Cottage LB | Wood Lane Road, near High Barn Cottage LB | 01CHR0012 | CHR0012A | SO | SO on sewer network | SD5330915616 | GB112070064920 | Syd Brook | SYD BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1583
United Utilities | BROOK LANE PUMPING STATION | Brook Lane PS | 017091517 | CHR0033 | SO | Storm discharge at pumping station | SD5492015780 | GB112070064920 | Syd Brook via unknown trib | unnamed tributary of Syd Brook | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 361.27 | 51 | 44.2 | 5 (installed 2018) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1584
United Utilities | ROBIN HOOD PUMPING STATION | Robin Hood PS | 017091516 | CHR0046 | SO | Storm discharge at pumping station | SD5062016350 | GB112070064920 | Syd Brook | UNNAMED TRIB OF SYD BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 174.08 | 51 | 81.4 | 5 (installed 2018) | 99.85 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1585
United Utilities | ECCLESTONE BRIDGE CSO 12065 | Eccleston Bridge D/S CSO | 017060128 | CHR0051 | SO | SO on sewer network | SD5085017690 | GB112070064861 | Yarrow Culbeck Brook to tidal | RIVER YARROW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1773.81 | 109 | 137.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1586
United Utilities | BLACKMOOR ROAD CSO | Blackmoor Road CSO | NPSWQD010939 | CHR0063 | SO | SO on sewer network | SD4825015290 | GB112070064820 | Douglas - Lower | NEW REED BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 55.39 | 60 | 76.5 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1587
United Utilities | WARRINGTON NORTH WWTW | WARRINGTON NORTH WwTW | 016983122 | 16983122 | ST | Storm tank at WwTW | SJ5804086890 | 170 |  | MERSEY ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1518.18 | 132 | 124 | 4 (installed 2019) | 100 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1588
United Utilities | HALL NOOK COMBINED SEWER OVERFLOW | Hall Nook CSO (481XO) (WAR0007) | 01WAR0007 | WAR0007 | SO | SO on sewer network | SJ5666487360 | 170 |  | PENKETH BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 188.63 | 93 | 80.6 | 5 (installed 2018) | 99.72 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1589
United Utilities | CROSBY GARRET WWTW | Crosby Garret WwTW | 017670005 | 17670005 | SO | Inlet SO at WwTW | NY7277010050 | GB102076070790 | Blind Beck | CROSBY GARRETT BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 475.5 | 42 | 174.6 | 5 (installed 2018) | 100 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1590
United Utilities | CREWE WWTW | CREWE WwTW | 016810068 | 16810068 | ST | Storm tank at WwTW | SJ6664057110 | GB112068060460 | Weaver (Marbury Brook to Dane) | RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1352.68 | 109 | 87.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1591
United Utilities | JUNC HUNGERFORD ROAD AND LAURESTON | Junction of Hungerford Road and Laureston Avenue CSO | 01CRE0017 | CRE0017 | SO | SO on sewer network | SJ7200055500 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | DRAIN, TRIB OF VALLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 20.1 | 25 | 17.6 | 5 (installed 2018) | 89.79 | Sensor failure / issue | Resolved - May |  |  |  | UUG1592
United Utilities | PUSEY DALE PS | Pusey Dale PS | 016920239 | CRE0019 | SO | Storm discharge at pumping station | SJ6950351668 | GB112069064520 | Wistaston Brook | Tributary of Wistaston Brook | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 13.32 | 3 | 4.25 | 4 (installed 2019) | 100 | [5 empty] | UUG1593
United Utilities | FRANK WEBB AVENUE CSO | Frank Webb Avenue CSO | 016810300 | CRE0026 | SO | SO on sewer network | SJ6931056820 | GB112068060460 | Weaver (Marbury Brook to Dane) | LEIGHTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 11.41 | 8 | 6.75 | 4 (installed 2019) | 99.5 | [5 empty] | UUG1594
United Utilities | BRADELEY HALL ROAD CSO | Bradeley Hall Road CSO | 016810325 | CRE0027 | SO | SO on sewer network | SJ7283056220 | GB112068055400 | Fowle Brook | FOWLE BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 37.53 | 28 | 29 | 3 (installed 2020) | 97.61 | [5 empty] | UUG1595
United Utilities | QUEENS PARK (NO 1) | Queens Park Drive (Crewe) CSO | 01CRE0031 | CRE0031 | SO | SO on sewer network | SJ6856055440 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 114.99 | 43 | 39.75 | 4 (installed 2019) | 84.2 | Sensor failure / issue | N/A - Ongoing investigation | Data collection - EDM non-representative location | Resolved - Jan |  | UUG1596
United Utilities | QUEENS PARK NO 2 CSO | Queens Park Golf Club CSO | 01CRE0032 | CRE0032 | SO | SO on sewer network | SJ6850055420 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.47 | 1 | 5 | 4 (installed 2019) | 100 | [5 empty] | UUG1597
United Utilities | DENVER AVENUE ALTON STREET CSO | DENVER AVENUE / ALTON STREET CSO | 01CRE0034 | CRE0034 | SO | SO on sewer network | SJ6990055340 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 4.3 | 15 | 15.6 | 5 (installed 2018) | 100 | [5 empty] | UUG1598
United Utilities | ALTON STREET NO 2 CSO 161BP | Alton Street No.2 CSO | 01CRE0035 | CRE0035 | SO | SO on sewer network | SJ6996055310 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 816.8 | 48 | 20 | 4 (installed 2019) | 100 |  |  | Data collection - EDM non-representative location | N/A - Ongoing investigation |  | UUG1599
United Utilities | FLAG LANE N0 2 CSO 165JH | FLAG LANE No1 CSO | 01CRE0036 | CRE0036 | SO | SO on sewer network | SJ7003055320 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 14.4 | 28 | 21.6 | 5 (installed 2018) | 100 | [5 empty] | UUG1600
United Utilities | ALTON ST COMBINED SEWER OVERFLOW | Alton Street CSO | 016892334 | CRE0033 | SO | SO on sewer network | SJ6984055350 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.97 | 4 | 3.25 | 4 (installed 2019) | 100 | [5 empty] | UUG1601
United Utilities | FLAG LANE N0 2 CSO 165JH | FLAG LANE NO2 CSO | 01CRE0037 | CRE0037 | SO | SO on sewer network | SJ7003055320 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.33 | 1 | 5.4 | 5 (installed 2018) | 99.89 | [5 empty] | UUG1602
United Utilities | WISTASTON ROAD CSO | Wistaston Road CSO | 01CRE0038 | CRE0038 | SO | SO on sewer network | SJ6975055440 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 14 | 5 (installed 2018) | 100 | [5 empty] | UUG1603
United Utilities | EDLESTON ROAD NO 2 CSO | EDLESTON ROAD No1 CSO | 01CRE0040 | CRE0040 | SO | SO on sewer network | SJ7052055320 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2.9 | 5 | 21.6 | 5 (installed 2018) | 85.78 | Sensor failure / issue | Resolved - Oct |  |  |  | UUG1604
United Utilities | EDLESTON ROAD NO 2 CSO | Edleston Road No 2 CSO | 016892253 | CRE0041 | SO | SO on sewer network | SJ7052055320 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 2 | 4 (installed 2019) | 99.98 | [5 empty] | UUG1605
United Utilities | CHURCH LANE CREWE CSO | CHURCH LANE CSO (Crewe) | 01CRE0043 | CRE0043 | SO | SO on sewer network | SJ6850054290 | GB112068055280 | Wistaston Brook | WISTATON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 611.96 | 106 | 88 | 4 (installed 2019) | 95.2 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1606
United Utilities | MILL STREET CSO CREWE 169CW | MILL STREET CSO | 01CRE0042 | CRE0042 | SO | SO on sewer network | SJ7066055300 | GB112068055310 | Valley Brook (Englesea Brook to Weaver) | VALLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0.6 | 5 (installed 2018) | 91.51 | [5 empty] | UUG1607
United Utilities | BRIDGE STREET CSO | Bridge Street CSO | EPR/WB3294EP | CRE0099 | SO | SO on sewer network | SJ7012349593 | GB112068055240 | Checkley Brook - Lower | WYBUNBURY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0 | 4 (installed 2019) | 100 | [5 empty] | UUG1608
United Utilities | THORNTON ROAD DEPOT CSO 482U7 | Thornton Road Depot CSO | 01WAR0013 | WAR0013 | SO | SO on sewer network | SJ5776087340 | 170 |  | SANKEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 51.2 | 45 | 73 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1609
United Utilities | SANKEY BRIDGES PS | Sankey Bridge PS | 01WAR0028 | WAR0028 | SO | Storm discharge at pumping station | SJ5855087620 | 170 |  | SANKEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 8.37 | 10 | 15.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1610
United Utilities | COTEBROOK STW SO | COTEBROOK SO | 016810067 | 16810067 | SO | Inlet SO at WwTW | SJ5737065609 | GB112068060440 | Ash Brook (Source to Darley Brook) | Sandyford Brook | N/A | N/A | Not Applicable | Dec 2023 | 63.18 | 8 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1611
United Utilities | COTEHILL WWTW | Cote Hill Wastewater Treatment Works (COTHL) (017670051) | 017670051 | 17670051 | ST | Storm tank at WwTW | NY4692050960 | GB102076073910 | Pow Maughan Beck | POW MAUGHAN BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 450.02 | 88 | 80.6 | 5 (installed 2018) | 99.96 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1612
United Utilities | CONISTON WWTW | Coniston WwTW | 017370035 | 17370035 | ST | Storm tank at WwTW | SD3072097050 | GB112073071210 | Yewdale/Church Beck | CHURCH BECK | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 3389.66 | 178 | 168.8571 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1613
United Utilities | CONGLETON STW | CONGLETON WwTW | 016810066 | 16810066 | SO | Inlet SO at WwTW | SJ8538263482 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 92.49 | 31 | 7.75 | 4 (installed 2019) | 99.36 | [5 empty] | UUG1614
United Utilities | CONGLETON STW | CONGLETON WwTW | 016810066 | 16810066 | ST | Storm tank at WwTW | SJ8538263482 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 326.92 | 65 | 16.25 | 4 (installed 2019) | 85.74 | Comms failure / issue | Resolved - Dec | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1615
United Utilities | EATON BANK CSO 131S4 | Eaton Bank CSO | 01CON0004 | CON0004 | SO | SO on sewer network | SJ8674063840 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 163.2 | 89 | 82 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1616
United Utilities | DANE STREET CSO 131Q1 | DANE STREET CSO | 01CON0001 | CON0001 | SO | SO on sewer network | SJ8542063220 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.33 | 1 | 0.2 | 5 (installed 2018) | 100 | [5 empty] | UUG1617
United Utilities | BERISFORDS COMPOUND CSO 131G3 | BERISFORDS COMPOUND CSO | 01CON0029 | CON0029 | SO | SO on sewer network | SJ8650063570 | GB112068055360 | Biddulph Brook | DANE IN SHAW BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 94.03 | 60 | 63.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1618
United Utilities | BROMLEY RD CORONATION RD CSO 131GZ | BROMLEY ROAD / CORONATION ROAD CSO | 01CON0031 | CON0031 | SO | SO on sewer network | SJ8638063260 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1070.43 | 98 | 72.8 | 5 (installed 2018) | 98.91 |  |  | Data collection - EDM non-representative location | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1619
United Utilities | THE GRANGE CONGLETON CSO | The Grange (Congleton) Combined Sewer Overflow (Site ID 132UW) (CON0032) | 01CON0032 | CON0032 | SO | SO on sewer network | SJ8604063240 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 105.5 | 65 | 54 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1620
United Utilities | CASTLE INN ROAD MOSSLEY CSO | Castle Inn Road (Mossley) Combined Sewer Overflow (Site ID 13531) (CON0034) | 016892193 | CON0034 | SO | SO on sewer network | SJ8833061430 | GB112068055360 | Biddulph Brook | TRIB OF DANE-IN-SHAW BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 94.93 | 29 | 10 | 4 (installed 2019) | 99.98 | [5 empty] | UUG1621
United Utilities | MILL LANE CSO (134I5) | MILL LANE CSO | 01CON0035 | CON0035 | SO | SO on sewer network | SJ8837061520 | GB112068055360 | Biddulph Brook | Dane in Shaw Brook | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 131.83 | 56 | 43.3333 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1622
United Utilities | HAVANNAH STREET/ REDFERN AVE CSO | Havannah Street/Redfern Avenue Combined Sewer Overflow | 016892194 | CON0037 | SO | SO on sewer network | SJ8678763891 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 11.5 | 11 | 18.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1623
United Utilities | BROMLEY ROAD CSO | Bromley Road CSO | 016892195 | CON0038 | SO | SO on sewer network | SJ8670063170 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 3.73 | 16 | 19 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1624
United Utilities | WEST HEATH PUMPING STATION | West Heath pumping station (13542) (CON0058) | 016981657 | CON0058 | SO | Storm discharge at pumping station | SJ8342063090 | GB112068055370 | Loach Brook | LOACH BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 641.39 | 72 | 55.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1625
United Utilities | SPRAGG ST WILLOW ST CSO CON0089 | Spragg Street/ Willow Street CSO | EPRJB3896RV | CON0089 | SO | SO on sewer network | SJ8630863019 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE | N/A | N/A | Not Applicable | Dec 2023 | 1868.13 | 141 |  | <1 yr (installed 2023) | 95.2055 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1626
United Utilities | SEFTON AVENUE CSO (CON0090) | Sefton Avenue combined sewer overflow | EPRJB3896NC | CON0090 | SO | SO on sewer network | SJ8703062334 | GB112068060190 | Dane (Cow Brook to Wheelock) | RIVER DANE VIA S/WATER SEWER | N/A | N/A | Not Applicable | Dec 2023 | 21.67 | 39 |  | <1 yr (installed 2023) | 96.5217 | [5 empty] | UUG1627
United Utilities | WHITEGATES PUMPING STATION | Whitegates pumping station (41004) (STA0099) | 016881660 | STA0099 | SO | Storm discharge at pumping station | SJ8874060170 | GB112068055360 | Biddulph Brook | BIDDULPH BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2.48 | 6 | 13.2 | 5 (installed 2018) | 100 | [5 empty] | UUG1628
United Utilities | WHITEMORE PUMPING STATION | Whitemore PS | 016881659 | STA0100 | SO | Storm discharge at pumping station | SJ8855061170 | GB112068055360 | Biddulph Brook | BIDDULPH BROOK, TRIB RVR DANE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 783.16 | 82 | 54 | 5 (installed 2018) | 100 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1629
United Utilities | COLNE WASTE WATER TREATMENT WORKS | Colne WwTW | 017160006 | 17160006 | ST | Storm tank at WwTW | SD8703039470 | GB112071065200 | Colne Water - Trawden Bk to Wanless Water | COLNE WATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 922.14 | 113 | 113 | 3 (installed 2020) | 91.75 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1630
United Utilities | LANESHAWBRIDGE SCHOOL LANE CSO | Laneshawbridge School Lane Combined Sewer Overflow | 01PEN0029 | PEN0029 | SO | SO on sewer network | SD9230040670 | GB112071065210 | Colne Water (Laneshaw) | COLNE WATER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.57 | 5 | 7 | 4 (installed 2019) | 98.82 | [5 empty] | UUG1631
United Utilities | COLNE REFUSE TRANSFER STATION | Colne Refuse Transfer Station CSO (Site ID 322YC) (PEN0059) | 01PEN0059 | PEN0059 | SO | SO on sewer network | SD8749039380 | GB112071065200 | Colne Water - Trawden Bk to Wanless Water | COLNE WATER | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 95.33 | 32 | 30.3333 | 6 (installed 2017) | 100 | [5 empty] | UUG1632
United Utilities | COCKERMOUTH WWTW | COCKERMOUTH WwTW | 017570031 | 17570031 | ST | Storm tank at WwTW | NY1024031140 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2939.37 | 172 | 34.4 | 5 (installed 2018) | 99.72 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | Resolved - January after reporting year | Other investigation - non-WINEP/Green Recovery | UUG1633
United Utilities | THE BURROUGHS CSO 022UQ | The Burroughs CSO | 01ALL0023 | ALL0023 | SO | SO on sewer network | NY1091031050 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 53.33 | 38 | 42.8 | 5 (installed 2018) | 99.99 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1634
United Utilities | FITZ BRIDGE (LOW ROAD) CSO | Fitz Bridge (Low Road) CSO | 017571047 | ALL0063 | SO | SO on sewer network | NY1068030860 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1212.18 | 102 | 109.6 | 5 (installed 2018) | 77.94 | Sensor failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1635
United Utilities | BELLE VUE /COCKERMOUTH PS | Belle Vue (Cockermouth) PS | 017580263 | ALL0112 | SO | Storm discharge at pumping station | NY1025031180 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 136.45 | 30 | 53 | 5 (installed 2018) | 99.62 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1636
United Utilities | BRIGHAM PUMPING STATION (ALL0138) | Brigham Pumping Station | EPRJB3597NK | ALL0138 | SO | Storm discharge at pumping station | NY0838630592 | GB112075070520 | Derwent - conf Cocker to tidal | STONY BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 41.03 | 24 | 28 | 3 (installed 2020) | 99.69 | [5 empty] | UUG1637
United Utilities | PAPCASTLE PUMPING STATION (ALL0139) | Papcastle Pumping Station | EPRJB3597VV | ALL0139 | SO | Storm discharge at pumping station | NY1035931293 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.21 | 4 | 6.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG1638
United Utilities | VICARAGE LANE CSO 022WD | Vicarage Lane | 017580253 | ALL0097 | SO | SO on sewer network | NY1275030230 | GB112075070390 | Tom Rudd Beck | TOM RUDD BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0.6 | 5 (installed 2018) | 100 | [5 empty] | UUG1639
United Utilities | WHITTLE BROOK PS | Whittle Brook PS | 01WAR0048 | WAR0048 | SO | Storm discharge at pumping station | SJ5773087300 | 170 |  | MERSEY ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 49.17 | 39 | 28.5 | 4 (installed 2019) | 99.98 | [5 empty] | UUG1640
United Utilities | CLITHEROE WWTW | CLITHEROE WwTW | 017160033 | 17160033 | ST | Storm tank at WwTW | SD7262040390 | GB112071065510 | Mearley Brook | BARROW CLOUGH/PENDLETON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1786.34 | 129 | 32.25 | 4 (installed 2019) | 94.1 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1641
United Utilities | ADJ POLICE STATION KING STREET CSO | ADJ POLICE STATION KING STREET CSO | 01RIB0002 | RIB0002 | SO | SO on sewer network | SD7313041110 | GB112071065510 | Mearley Brook | TRIB OF PENDLETON BROOK BY SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.23 | 2 | 13.75 | 4 (installed 2019) | 100 | [5 empty] | UUG1642
United Utilities | NORTH WEST OF HENTHORN ROAD BRIDGE | North West of Henthorn Road Bridge (EO for Lower Moor PS) | 017160099 | RIB0027 | SO | Storm discharge at pumping station | SD7270040600 | GB112071065510 | Mearley Brook | PENDLETON BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 465.9 | 70 | 60.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1643
United Utilities | CLITHEROE STREET CSO | Clitheroe Street CSO | 017160177 | RIB0030 | SO | SO on sewer network | SD7330040560 | GB112071065510 | Mearley Brook | PENDLETON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 291.5 | 71 | 48 | 4 (installed 2019) | 98.48 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1644
United Utilities | WEST BRADFORD PS | West Bradford WwNPS | 01RIB0031 | RIB0031 | SO | Storm discharge at pumping station | SD7455044190 | GB112071065612 | Ribble DS Stock Beck | WEST BRADFORD BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 538.84 | 73 | 58 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1645
United Utilities | CHATBURN PUMPING STATION | Chatburn (Ribble Lane) PS | NPSWQD005629 | RIB0051 | SO | Storm discharge at pumping station | SD7678044720 | GB112071065612 | Ribble DS Stock Beck | CHATBURN BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1253.75 | 105 | 96.3333 | 3 (installed 2020) | 92.01 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1646
United Utilities | CLEATOR WWTW | CLEATOR WwTW | 017470025 | 17470025 | ST | Storm tank at WwTW | NY0129013190 | GB112074070000 | Keekle (lower) | RIVER KEEKLE | N/A | Seascale | Not Applicable | Commissioned in 2017 - full year data expected | 826.88 | 54 | 83.5 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1647
United Utilities | CLEATOR WWTW | CLEATOR WwTW | 017470025 | 17470025 | SO | Inlet SO at WwTW | NY0129013190 | GB112074070000 | Keekle (lower) | RIVER KEEKLE | N/A | Seascale | Not Applicable | Commissioned in 2017 - full year data expected | 3 | 13 | 2.1667 | 6 (installed 2017) | 99.99 | [5 empty] | UUG1648
United Utilities | ARLECDON COMBINED SEWER OVERFLOW | Arlecdon CSO | 017480418 | COP0001 | SO | SO on sewer network | NY0508018430 | GB112074070010 | Ehen (upper including Liza) | WINDER BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 6.7 | 10 | 10 | 4 (installed 2019) | 100 | [5 empty] | UUG1649
United Utilities | KILN BROW PUMPING STATION | Kiln Brow WwPS | 01COP0011 | COP0011 | SO | Storm discharge at pumping station | NY0165013401 | GB112074070010 | Ehen (upper including Liza) | RIVER EHEN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 451.54 | 24 | 26.6667 | 3 (installed 2020) | 84.7 | Sensor failure / issue | Resolved - May |  |  |  | UUG1650
United Utilities | LINETHWAITE PUMPING STATION | Linethwaite PS | 017480475 | COP0012 | SO | Storm discharge at pumping station | NX9917014000 | GB112074069990 | Pow Beck (South West Lakes) | NEEDLESS BECK | N/A | St Bees | Not Applicable | Commissioned in 2016 - full year data expected | 1.68 | 3 | 9.1429 | 7 (installed 2016) | 99.98 | [5 empty] | UUG1651
United Utilities | 28/29 ARLECDON PARKS ROAD CSO | Arlecdon Parks Road CSO to Winder Beck | 01COP0017 | COP0017 | SO | SO on sewer network | NY0514018660 | GB112074070010 | Ehen (upper including Liza) | TRIB OF WINDER BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 1 | 4 (installed 2019) | 100 | [5 empty] | UUG1652
United Utilities | ARLECDON PARKS ROAD CSO | Arlecdon Parks Road CSO | 017480419 | COP0018 | SO | SO on sewer network | NY0522018650 | GB112074070010 | Ehen (upper including Liza) | ELLER GILL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 37.27 | 38 | 42 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1653
United Utilities | KILN BROW COMBINED SEWER OVERFLOW | Kiln Brow CSO | 017480401 | COP0019 | SO | SO on sewer network | NY0165013400 | GB112074070010 | Ehen (upper including Liza) | RIVER EHEN | N/A | St Bees | Not Applicable | Commissioned in 2016 - full year data expected | 0.57 | 2 | 15.2857 | 7 (installed 2016) | 100 | [5 empty] | UUG1654
United Utilities | KEEKLE PUMPING STATION | Keekle PS | 017470076 | COP0058 | SO | Storm discharge at pumping station | NY0050016170 | GB112074070000 | Keekle (lower) | RIVER KEEKLE | N/A | Seascale | Not Applicable | Commissioned in 2017 - full year data expected | 1290.29 | 157 | 113.8333 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1655
United Utilities | NORBECK PARK A CSO (SITE 023A9) | Norbeck Park A CSO | 017480286 | COP0083 | SO | SO on sewer network | NY0114015370 | GB112074070000 | Keekle (lower) | NORBECK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 31.57 | 60 | 66.1667 | 6 (installed 2017) | 97.09 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1656
United Utilities | BLIND LANE CSO 02627 | Blind Lane CSO | 017580238 | COP0089 | SO | SO on sewer network | NY0083014640 | GB112074070000 | Keekle (lower) | RIVER KEEKLE | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 286.42 | 41 | 42 | 6 (installed 2017) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1657
United Utilities | MOOR ROAD COMBINED SEWER OVERFLOW | Moor Row CSO | 017580237 | COP0090 | SO | SO on sewer network | NY0096014430 | GB112070064952 | Yarrow DS Big Lodge Water | RIVER KEEKLE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 220.67 | 89 | 86.2 | 5 (installed 2018) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1658
United Utilities | BROOKSIDE CSO | Brookside CSO | 017580239 | COP0091 | SO | SO on sewer network | NY0211013960 | GB112074070010 | Ehen (upper including Liza) | RIVER EHEN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 345.2 | 90 | 82 | 3 (installed 2020) | 99.95 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1659
United Utilities | REAR GARDEN OF 16 CROSSINGS CLOSE | Rear Garden of No.16 Crossings Close | 017480387 | COP0095 | SO | SO on sewer network | NY0114015360 | GB112074070000 | Keekle (lower) | NOR BECK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1660
United Utilities | AUSTWICK PUMPING STATION CRA0010 | Austwick SPS | EPREP3526GE | CRA0010 | SO | Storm discharge at pumping station | SD7642067270 | GB112072066090 | Fen Beck | TRIB FEN BECK VIA DRYING BEDS | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 1971.83 | 103 | 90.4286 | 7 (installed 2016) | 99.97 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | U_INV driver - Stage 4: No cost beneficial solution | UUG1661
United Utilities | CLAPHAM WASTEWATER TREATMENT WORKS | Clapham WwTW | EPREP3526XK | EPREP3526XK | ST | Storm tank at WwTW | SD7444068690 | GB112072071840 | Clapham Beck | RIVER WENNING | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 376.36 | 61 | 23 | 3 (installed 2020) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1662
United Utilities | CHORLEY WASTE WATER TREATMENT WORKS | Chorley WwTW | 017060016 | 17060016 | ST | Storm tank at WwTW | SD5638217462 | GB112070064952 | Yarrow DS Big Lodge Water | RIVER YARROW & CHOR | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 193.8 | 36 | 53.3333 | 3 (installed 2020) | 96.93 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1663
United Utilities | EARLS WAY CSO 12066 | Earls Way CSO | 01CHR0002 | CHR0002 | SO | SO on sewer network | SD5580018890 | GB112070064861 | Yarrow Culbeck Brook to tidal | CHAPEL BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 222.55 | 83 | 84 | 5 (installed 2018) | 36.84 | Sensor failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1664
United Utilities | Park Avenue CSO (to Chapel Brook) | Park Avenue CSO (to Chapel Brook) | 017190821 | CHR0004 | SO | SO on sewer network | SD5559018880 | GB112070064861 | Yarrow Culbeck Brook to tidal | RIVER YARROW & CHAPEL BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 200.95 | 63 | 56.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1665
United Utilities | Park Avenue CSO (to Chapel Brook) | Park Avenue CSO (to Chapel Brook) | 017190821 | CHR0004 | SO | SO on sewer network | SD5526117906 | GB112070064861 | Chapel Brook | RIVER YARROW & CHAPEL BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 82.82 | 46 | 38.8 | 5 (installed 2018) | 99.99 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1666
United Utilities | COWLING BROW CSO CHORL | Cowling Brow CSO | 01CHR0009 | CHR0009 | SO | SO on sewer network | SD5956016940 | GB112070064951 | Yarrow US Big Lodge Water | BLACK BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 121.83 | 57 | 72.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1667
United Utilities | FRIDAY STREET CSO 121UY | FRIDAY STREET CSO | 01CHR0010 | CHR0010 | SO | SO on sewer network | SD5820017890 | GB112070064952 | Yarrow DS Big Lodge Water | RIVER CHOR | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0.6 | 5 (installed 2018) | 96.28 | [5 empty] | UUG1668
United Utilities | HEAPEY ROAD CSO 121YP | Heapey CSO | 01CHR0013 | CHR0013 | SO | SO on sewer network | SD6001018920 | GB112070064951 | Yarrow US Big Lodge Water | BLACK BROOK, TRIB OF R YARROW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.13 | 1 | 1.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1669
United Utilities | EAVES GREEN RD CSO | Eaves Green Brook CSO | 01CHR0016 | CHR0016 | SO | SO on sewer network | SD5783015960 | GB112070064952 | Yarrow DS Big Lodge Water | TRIB RIVER YARROW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 18.27 | 25 | 19.6 | 5 (installed 2018) | 100 | [5 empty] | UUG1670
United Utilities | 96 COLLINGWOOD ROAD CSO 121PB | 96 COLLINGWOOD ROAD CSO | 01CHR0017 | CHR0017 | SO | SO on sewer network | SD5750017000 | GB112070064952 | Yarrow DS Big Lodge Water | CLVRTED TRIB RIVER CHOR | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 8.37 | 25 | 23.6667 | 6 (installed 2017) | 100 | [5 empty] | UUG1671
United Utilities | PARKLANDS CSO 123JR CHR0015 | Parklands CSO | 017081354 | CHR0015 | SO | SO on sewer network | SD5694017740 | GB112070064952 | Yarrow DS Big Lodge Water | RIVER CHOR TRIB RIVER YARROW | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0.27 | 2 | 1.5 | 6 (installed 2017) | 100 | [5 empty] | UUG1672
United Utilities | O/S 8 HARDY DRIVE CSO | O/S 8 HARDY DRIVE CSO | 01CHR0018 | CHR0018 | SO | SO on sewer network | SD5732017020 | GB112070064952 | Yarrow DS Big Lodge Water | TRIB RIVER CHOR | N/A | N/A | Not Applicable | Dec 2023 | 234.87 | 126 |  | <1 yr (installed 2023) | 100 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1673
United Utilities | CLOVER ROAD BUTTERWORTH BROW CSO | Clover Road/Butterworth Brow CSO | 01CHR0023 | CHR0023 | SO | SO on sewer network | SD5683015940 | GB112070064952 | Yarrow DS Big Lodge Water | SWS TO RIVER YARROW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 290.18 | 95 | 71.8 | 5 (installed 2018) | 99.93 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1674
United Utilities | ADJ DUXBURY MILL P.S. CSO ID 12006 | Adjacent Duxbury Mill Pumping Station Combined Sewer Overflow (CHR0024) | 01CHR0024 | CHR0024 | SO | SO on sewer network | SD5882015660 | GB112070064951 | Yarrow US Big Lodge Water | RIVER YARROW | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 251.83 | 82 | 68.3333 | 6 (installed 2017) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1675
United Utilities | CLOVER ROAD PUMPING STATION | Clover Road PS | 017081574 | CHR0027 | SO | Storm discharge at pumping station | SD5685015890 | GB112070064952 | Yarrow DS Big Lodge Water | RIVER YARROW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 52.37 | 17 | 40.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1676
United Utilities | LIMBRICK PUMPING STATION | Limbrick Pumping Station (12024) (CHR0030) | 01CHR0030 | CHR0030 | SO | Storm discharge at pumping station | SD6003016340 | GB112070064951 | Yarrow US Big Lodge Water | RIVER YARROW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 3.36 | 9 | 15 | 5 (installed 2018) | 99.95 | [5 empty] | UUG1677
United Utilities | GLENCROFT PUMPING STATION | Glencroft PS | 017091518 | CHR0028 | SO | Storm discharge at pumping station | SD5500019000 | GB112070064861 | Yarrow Culbeck Brook to tidal | RANSNAP BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0.75 | 4 (installed 2019) | 96.07 | [5 empty] | UUG1678
United Utilities | LYDD GROVE PS | Lydd Grove PS | 017091508 | CHR0038 | SO | Storm discharge at pumping station | SD5701017010 | GB112070064952 | Yarrow DS Big Lodge Water | UNNAMED TRIB OF RIVER CHOR | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 10.86 | 12 | 14.25 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1679
United Utilities | BAGANLEY FROOM CSO 121CW | Baganley Froom CSO | 01CHR0049 | CHR0049 | SO | SO on sewer network | SD5691017960 | GB112070064952 | Yarrow DS Big Lodge Water | BLACK BROOK TRIB RIVER YARROW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 367.27 | 62 | 38.6 | 5 (installed 2018) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1680
United Utilities | COPPULL NEW RD/BUTTERWORTH RD CSO | Coppull New Road/Butterworth Brow CSO | 017081147 | CHR0050 | SO | SO on sewer network | SD5685015931 | GB112070064952 | Yarrow DS Big Lodge Water | RIVER YARROW | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 439.2 | 110 | 107 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1681
United Utilities | Duxbury Mill Farm PS | Duxbury Mill Farm PS | EPRSB3395VW | CHR0059 | SO | Storm discharge at pumping station | SD5881715661 | GB112070064951 | Yarrow US Big Lodge Water | River Yarrow | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.32 | 1 | 3.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1682
United Utilities | EAVES GREEN RD CSO | Eaves Green Road CSO | 01LA1964 | CHR0066 | SO | SO on sewer network | SD5783015960 | GB112070064952 | Yarrow DS Big Lodge Water | TRIB RIVER YARROW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 52.17 | 43 | 42.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1683
United Utilities | MOOR ROAD EAVES GREEN RD CSO 122GB | Moor Road/Eaves Green Road CSO | 017081255 | CHR0087 | SO | SO on sewer network | SD5683015941 | GB112070064952 | Yarrow DS Big Lodge Water | RIVER YARROW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 41.57 | 62 | 76.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1684
United Utilities | COMMON BANK LANE CSO CHORL | Common Bank Lane CSO | 017081355 | CHR0090 | SO | SO on sewer network | SD5678017740 | GB112070064952 | Yarrow DS Big Lodge Water | RIVER CHOR DIVERSION CHANNEL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.73 | 2 | 2.2 | 5 (installed 2018) | 100 | [5 empty] | UUG1685
United Utilities | CHORLEY LOWER WORKS PS | Chorley Lower Works PS | 017081342 | CHR0091 | SO | Storm discharge at pumping station | SD5638017460 | GB112070064952 | Yarrow DS Big Lodge Water | RIVER YARROW | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 299.35 | 45 | 55.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1686
United Utilities | ST MARYS CHURCH (CHIPPING) CSO | ST MARYS CHURCH CSO | 01RIB0005 | RIB0005 | SO | SO on sewer network | SD6236043300 | GB112071065330 | Chipping Brook | CHIPPING BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 2.17 | 10 | 10.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG1687
United Utilities | CHAPEL-EN-LE-FRITH WWTW | CHAPEL-EN-LE-FRITH WwTW | 016940168 | 16940168 | ST | Storm tank at WwTW | SK0481082020 | GB112069060910 | Black Brook (Upper Mersey) | BLACK BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 2136.82 | 174 | 158.3333 | 6 (installed 2017) | 99.95 |  |  | Data collection - EDM non-representative location | resolved - Oct | U_INV driver - Stage 4: No cost beneficial solution | UUG1688
United Utilities | BOWDEN LANE CSO 211FL | Bowden Lane CSO | 016940364 | PEA0025 | SO | SO on sewer network | SK0597181521 | GB112069060910 | Black Brook (Upper Mersey) | BLACK BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 359.03 | 96 | 84.3333 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1689
United Utilities | MANC' ROAD (CHAPEL-EN-LE-FRITH) CSO | Manchester Road | 01PEA0048 | PEA0048 | SO | SO on sewer network | SK0504080460 | GB112069060860 | Randall Carr Brook | COMBS RESERVOIR | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 45.7 | 30 | 30.75 | 4 (installed 2019) | 100 | [5 empty] | UUG1690
United Utilities | CATON WASTEWATER TREATMENT WORKS | CATON WwTW | 017270001 | 17270001 | ST | Storm tank at WwTW | SD5277065250 | GB112072065980 | Lune - conf Wenning to tidal | RIVER LUNE | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 1554.86 | 96 | 92.8571 | 7 (installed 2016) | 57.41 | Comms failure / issue | Resolved - January after reporting year | Performance - Other maintenance / capital works (e.g. jetting) | Resolved - Jun | Other investigation - non-WINEP/Green Recovery | UUG1691
United Utilities | BULL BECK BROOKHOUSE CSO | Bull Beck Brookhouse Combined Sewer Overflow (Site ID 251HH) (LAN0089) | 017280284 | LAN0089 | SO | SO on sewer network | SD5408064800 | GB112072065980 | Lune - conf Wenning to tidal | BULL BECK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 7.13 | 5 | 5.5 | 6 (installed 2017) | 100 | [5 empty] | UUG1692
United Utilities | THURTELL COTTAGES CSO LAN0091 | Thurtell Cottages CSO | 01LAN0091 | LAN0091 | SO | SO on sewer network | SD5280065240 | GB112072065980 | Lune - conf Wenning to tidal | RIVER LUNE | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 36.83 | 41 | 37.2857 | 7 (installed 2016) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1693
United Utilities | ARTLEBECK COMBINED SEWER OVERFLOW | Artle Beck Road CSO | 017280359 | LAN0108 | SO | SO on sewer network | SD5345064650 | GB112072065960 | Artle Beck | ARTLE BECK | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 2.17 | 9 | 9.5714 | 7 (installed 2016) | 100 | [5 empty] | UUG1694
United Utilities | ARTLE BECK COMBINED SEWER OVERFLOW | Artle Beck CSO | 017290459 | LAN0119 | SO | SO on sewer network | SD5339064880 | GB112072065960 | Artle Beck | ARTLE BECK, TRIB OF RIVER LUNE | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 5.13 | 6 | 24.4286 | 7 (installed 2016) | 93.55 | [5 empty] | UUG1695
United Utilities | CASTLETON WWTW CSTLT | CASTLETON WwTW | 016950034 | 16950034 | ST | Storm tank at WwTW | SD8803009580 | GB112069061161 | Irk (Sourtce to Wince Brook) | TRUB BROOK TRIB RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1336.62 | 123 | 137.4 | 5 (installed 2018) | 99.44 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Resolved - Dec | Other investigation - non-WINEP/Green Recovery | UUG1696
United Utilities | CASTLETON SOUTH JUNCTION CSO | Adj M62 Castleton | 01ROC0094 | ROC0094 | SO | SO on sewer network | SD8814009780 | GB112069061161 | Irk (Sourtce to Wince Brook) | Culverted tributary of Trub Brook | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 170.87 | 62 | 55 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1697
United Utilities | CASTLE CARROCK WWTW | CASTLE CARROCK WwTW | 017670090 | 17670090 | SO | Inlet SO at WwTW | NY5409055900 | GB102076074040 | Gelt | CASTLE CARROCK BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 92.69 | 85 | 99.4 | 5 (installed 2018) | 98.9 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1698
United Utilities | CASTLE CARROK CSO | Castle Carrok CSO (Adjacent Donlea House) | 017680315 | CAR0069 | SO | SO on sewer network | NY5422055720 | GB102076074040 | Gelt | CASTLE CARROCK BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 4.6 | 11 | 15.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG1699
United Utilities | CASTERTON WWTW | CASTERTON WwTW | 017270014 | 17270014 | ST | Storm tank at WwTW | SD6176079550 | GB112072071690 | Lune - conf Rawthey to conf Greta | RIVER LUNE | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 34.49 | 14 | 8.4286 | 7 (installed 2016) | 99.96 | [5 empty] | UUG1700
United Utilities | THEWLIS STREET CSO | Thewlis Street CSO | 01WAR0060 | WAR0060 | SO | SO on sewer network | SJ5950087910 | 170 |  | RIVER MERSEY | N/A | N/A | Not Applicable | Dec 2023 | 7.14 | 15 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1701
United Utilities | GARDNER ROAD PUMPING STATION | Gardner Road Pumping Station (Site ID 25027) (LAN0058) | NPSWQD011000 | LAN0058 | SO | Storm discharge at pumping station | SD5003071450 | GB112073064430 | Keer - Lower | RIVER KEER | 115 Morecambe Bay East | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 1316.75 | 63 | 24.3333 | 6 (installed 2017) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1702
United Utilities | HAGG LANE MIDLAND TERRACE PS | Hagg Lane (Midland Terrace) PS | 01LAN0059 | LAN0059 | SO | Storm discharge at pumping station | SD4966071170 | GB112073064430 | Keer - Lower | RIVER KEER | 115 Morecambe Bay East | Morcambe North | Not Applicable | Commissioned in 2016 - full year data expected | 80.06 | 34 | 21.2857 | 7 (installed 2016) | 99.96 | [5 empty] | UUG1703
United Utilities | KNUTSFORD RD/GRAMMAR SCHOOL RD CSO | KNUTSFORD / GRAMMAR SCHOOL ROAD CSO | 01WAR0073 | WAR0073 | SO | SO on sewer network | SJ6269086950 | 169 |  | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 19.67 | 37 | 37 | 3 (installed 2020) | 85.71 | Comms failure / issue | Resolved - May |  |  |  | UUG1704
United Utilities | WARRINGTON SOUTH WWTW | WARRINGTON SOUTH WwTW | 016820128 | 16820128 | ST | Storm tank at WwTW | SJ5870085580 | 169 |  | M/C SHIP CANAL (TIDAL) | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 951.36 | 105 | 160 | 4 (installed 2019) | 85.43 | Comms failure / issue | Resolved - January after reporting year | Performance - Pump failure / issue | Resolved - Apr | Other investigation - non-WINEP/Green Recovery | UUG1705
United Utilities | FAIRFIELD RD RUSSELL RD CSO 25026 | Fairfield Road/Russell Road CSO | 01LAN0070 | LAN0070 | SO | Storm discharge at pumping station | SD5038070130 | GB112073064430 | Keer - Lower | CLVRT BACK LANE / KELLET RD | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0.4 | 5 (installed 2018) | 99.99 | [5 empty] | UUG1706
United Utilities | WALTON PS | WALTON PUMPING STATION | 016920316 | WAR0022 | SO | Storm discharge at pumping station | SJ6029086070 | 169 |  | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 271.41 | 43 | 42 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1707
United Utilities | CARLISLE WWTW | CARLISLE WwTW | 017670049 | 17670049 | SO | Inlet SO at WwTW | NY3847056520 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 276.96 | 56 | 11.2 | 5 (installed 2018) | 74.8 | Sensor failure / issue | Resolved - Dec | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1708
United Utilities | CARLISLE WWTW | CARLISLE WwTW | 017670049 | 17670049 | ST | Storm tank at WwTW | NY3847056520 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 734.53 | 60 | 62 | 5 (installed 2018) | 99.64 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1709
United Utilities | RICKERBY CSO | Rickerbys CSO | 017680296 | CAR0002 | SO | SO on sewer network | NY3997055031 | GB102076073880 | Caldew d/s Caldbeck | RIVER CALDEW | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0.33333 | 3 (installed 2020) | 97.07 | [5 empty] | UUG1710
United Utilities | B&Q CSO (101C4) | B&Q CSO | 017680294 | CAR0003 | SO | SO on sewer network | NY3997055030 | GB102076073880 | Caldew d/s Caldbeck | RIVER CALDEW | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 2.97 | 7 | 6 | 3 (installed 2020) | 98.08 | [5 empty] | UUG1711
United Utilities | ETTERBY TERRACE CSO | Etterby Terrace CSO | 01CAR0004 | CAR0004 | SO | SO on sewer network | NY3963057050 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 56.09 | 43 | 37 | 7 (installed 2016) | 99.98 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1712
United Utilities | LIME STREET SPS | Lime Street Wastewater Network Pumping Station | 017670160 | CAR0005 | SO | Storm discharge at pumping station | NY3999055350 | GB102076073880 | Caldew d/s Caldbeck | RIVER CALDEW | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 58.59 | 33 | 33.5 | 4 (installed 2019) | 99.97 | [5 empty] | UUG1713
United Utilities | STONEGARTH COMBINED SEWER OVERFLOW | STONEGARTH CSO | 01CAR0012 | CAR0012 | SO | SO on sewer network | NY3821054740 | GB102076073880 | Caldew d/s Caldbeck | DOW BECK CULVERT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 17.47 | 14 | 40.75 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1714
United Utilities | CAIRD AVENUE COMBINED SEWEROVERFLOW | Caird Avenue CSO | 017680416 | CAR0001 | SO | SO on sewer network | NY3855057430 | GB102076073940 | Eden - Eamont to tidal | POW BECK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0 | 4 (installed 2019) | 100 | [5 empty] | UUG1715
United Utilities | SCOTBY CSO | Scotby CSO | 017670159 | CAR0017 | SO | SO on sewer network | NY4330055810 | GB102076073940 | Eden - Eamont to tidal | COLLAR BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 76.4 | 26 | 21.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG1716
United Utilities | GILFORD PARK CSO (10542) | Gilford Park CSO | 017670037 | CAR0029 | SO | SO on sewer network | NY4138053680 | GB102076074030 | Petteril d/s Blackrack Beck | RIVER PETTERIL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 6.43 | 10 | 12.6667 | 3 (installed 2020) | 58.62 | Comms failure / issue | Resolved - January after reporting year |  |  |  | UUG1717
United Utilities | PETTERIL RAILWAY BRIDGE SSO | D/S Petterill Railway Bridge | 017670038 | CAR0030 | SO | SO on sewer network | NY4138055060 | GB102076074030 | Petteril d/s Blackrack Beck | RIVER PETTERIL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 14.97 | 12 | 6.3333 | 3 (installed 2020) | 99.27 | [5 empty] | UUG1718
United Utilities | CROWN STREET (TOWN DYKE ORCHARD | Crown Street (Town Dyke Orchard) Sewer | 017670204 | CAR0042 | SO | SO on sewer network | NY3968055830 | GB102076073880 | Caldew d/s Caldbeck | RIVER CALDEW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 36.8 | 37 | 30.8 | 5 (installed 2018) | 96.37 | [5 empty] | UUG1719
United Utilities | BOUSTEADS GRASSINGS CSO | Bousteads Grassing CSO | 01CAR0049 | CAR0049 | SO | SO on sewer network | NY3982054470 | GB102076073880 | Caldew d/s Caldbeck | RIVER CALDEW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 262.64 | 78 | 72.4 | 5 (installed 2018) | 99.95 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1720
United Utilities | STANWIX/STAINTON CSO | Stanwix and Stainton combined sewer overflow (Site ID 10009) (CAR0055) | 017670218 | CAR0055 | SO | SO on sewer network | NY3805056520 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 105.7 | 35 | 47.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1721
United Utilities | MELBOURNE PARK CSO | MELBOURNE PARK CSO | 017680278 | CAR0058 | SO | SO on sewer network | NY4159055340 | GB102076074030 | Petteril d/s Blackrack Beck | RIVER PETTERIL | N/A | Allonby | Not Applicable | Commissioned in 2018 - full year data expected | 30.73 | 17 | 16.2 | 5 (installed 2018) | 100 | [5 empty] | UUG1722
United Utilities | INFIRMARY STREET CARLISLE CSO | Infirmary Street (Carlisle) CSO | 017680309 | CAR0059 | SO | SO on sewer network | NY3883056370 | GB112071065270 | Eden - Eamont to tidal | Parham Beck | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 17.3 | 21 | 20.2 | 5 (installed 2018) | 99.96 | [5 empty] | UUG1723
United Utilities | FINN AVENUE COMBINED SEWER OVERFLOW | Finn Avenue CSO | 01CAR0013 | CAR0013 | SO | SO on sewer network | NY3926055620 | GB102076073880 | Caldew d/s Caldbeck | DOW BECK CULVERT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 49.8 | 52 | 14.4 | 5 (installed 2018) | 95.31 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1724
United Utilities | WARICK ROADWWNW PS | Warwick Road WwNPS | 017680359 | CAR0071 | SO | Storm discharge at pumping station | NY4180056080 | GB102076074030 | Petteril d/s Blackrack Beck | RIVER PETTERIL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 3.04 | 15 | 9 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1725
United Utilities | CARLETON MILL PUMPING STATION | Carleton Mill Pumping Station (10018) (CAR0074) | 017680319 | CAR0074 | SO | Storm discharge at pumping station | NY4290052560 | GB102076074030 | Petteril d/s Blackrack Beck | RIVER PETTERIL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 97.97 | 23 | 30.2 | 5 (installed 2018) | 85.67 | Sensor failure / issue | N/A - Ongoing investigation |  |  |  | UUG1726
United Utilities | RICKERBY PARK CSO | Rickerby Park CSO | 017680310 | CAR0060 | SO | SO on sewer network | NY4055056980 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected |  |  | 6.5714 | 7 (installed 2016) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1727
United Utilities | CROSBY ON EDEN PUMPING STATION | Low Crosby PS | 017680321 | CAR0076 | SO | Storm discharge at pumping station | NY4458059300 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0 | 0 | 0.33333 | 6 (installed 2017) | 100 | [5 empty] | UUG1728
United Utilities | REAR OF PIRELLI FACTORY CSO | Rear of Pirelli Factory CSO | 017680351 | CAR0088 | SO | SO on sewer network | NY3937053450 | GB102076073880 | Caldew d/s Caldbeck | RIVER CALDEW | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 6.67 | 20 | 22 | 3 (installed 2020) | 100 | [5 empty] | UUG1729
United Utilities | NEAR TRINITY SCHOOL | Trinity School / Strand Road Combined Sewer Overflow (Site ID 10015) xxxx ) (CAR0093) | 017680358 | CAR0093 | SO | SO on sewer network | NY4086056370 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 249.79 | 78 | 74.8571 | 7 (installed 2016) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1730
United Utilities | CARGO WASTEWATER TREATMENT WORKS | CARGO WwTW | 017670194 | 17670194 | SO | Inlet SO at WwTW | NY3610058800 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 2214.2 | 217 | 321.5 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1731
United Utilities | CSO ADJACENT TO CARGO WWTW CARGO | CSO adjacent to Cargo WwTW | 01CAR0016 | CAR0016 | SO | SO on sewer network | NY3599058850 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 143.5 | 78 | 79.6667 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1732
United Utilities | CAMERTON WWTW CAMER | CAMERTON WwTW | 017570030 | 17570030 | ST | Storm tank at WwTW | NY0298030100 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 3.6 | 5 (installed 2018) | 99.97 | [5 empty] | UUG1733
United Utilities | CAMERTON WW PUMPING STATION | Camerton Ww PS | 017580269 | ALL0118 | SO | Storm discharge at pumping station | NY0380030550 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 67.5 | 15 | 26 | 5 (installed 2018) | 100 | [5 empty] | UUG1734
United Utilities | CALTHWAITE WW PUMPING STATION | Calthwaite Ww Pumping Station (CALPumping Station) (EDE0036) | 01EDE0036 | EDE0036 | SO | Storm discharge at pumping station | NY5188029730 | GB102076071020 | Eamont (Upper) | DOG BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 29.95 | 17 | 18.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1735
United Utilities | CALDER BRIDGE WWTW | CALDER BRIDGE WwTW | 017470034 | 17470034 | SO | Inlet SO at WwTW | NY0367004920 | GB112074069730 | Calder (Lower) | RIVER CALDER | N/A | Seascale | Not Applicable | Commissioned in 2016 - full year data expected | 618.88 | 49 | 120 | 7 (installed 2016) | 70.19 | Comms failure / issue | Resolved - January after reporting year | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1736
United Utilities | CALDBECK WWTW | CALDBECK WwTW | 017670113 | 17670113 | ST | Storm tank at WwTW | NY3289039920 | GB102076073740 | Whelpo (Cald) Beck | CALD BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1108.59 | 96 | 90.4 | 5 (installed 2018) | 100 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1737
United Utilities | HESKET NEWMARKET PUMPING STATION | Hesket Newmarket Pumping Station (02509) (ALL0119) | 017680308 | ALL0119 | SO | Storm discharge at pumping station | NY3416038780 | GB102076073730 | Caldew (Hesket Newmarket) | RIVER CALDEW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 25 | 25 | 29.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1738
United Utilities | BURY WASTEWATER TREATMENT WORKS | BURY WwTW | 016950033 | 16950033 | SO | Inlet SO at WwTW | SD8004007810 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 36.8 | 5 (installed 2018) | 98.18 |  |  |  |  | U_INV driver - Stage 4: No cost beneficial solution | UUG1739
United Utilities | BURY WASTEWATER TREATMENT WORKS | BURY WwTW | 016950033 | 16950033 | ST | Storm tank at WwTW | SD8004007810 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1678.78 | 116 | 120.4 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1740
United Utilities | CARR STREET CSO 099BP | CARR STREET CSO | 01BRY0001 | BRY0001 | SO | SO on sewer network | SD7935016470 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 3.47 | 14 | 25.8 | 5 (installed 2018) | 100 | [5 empty] | UUG1741
United Utilities | NUTTALL HALL ROAD CSO | Nuttall Hall Road CSO | 016951212 | BRY0002 | SO | SO on sewer network | SD7958015630 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 481.97 | 101 | 93.7143 | 7 (installed 2016) | 96.07 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1742
United Utilities | PEEL HALL DRIVE CSO | Peel Hall Drive CSO | 01BRY0004 | BRY0004 | SO | SO on sewer network | SD7898014680 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 143.03 | 72 | 98.2857 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1743
United Utilities | BURNLEY ROAD CSO 099BL | BURNLEY ROAD CSO | 01BRY0006 | BRY0006 | SO | SO on sewer network | SD8041013840 | GB112069064620 | Irwell (Rossendale STW to Roch) | WALMERSLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 100.53 | 75 | 82.8 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1744
United Utilities | NEW STREET COMBINED SEWER OVERFLOW | NEW STREET CSO | 01BRY0008 | BRY0008 | SO | SO on sewer network | SD7779012790 | GB112069064610 | Kirklees Brook | BLACK BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 249.73 | 94 | 102.75 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1745
United Utilities | SEEDFIELD SECONDARY MODERN SCHL CSO | Seedfield Secondary Modern School CSO | 01BRY0010 | BRY0010 | SO | SO on sewer network | SD8037012230 | GB112069064620 | Irwell (Rossendale STW to Roch) | UNNAMED TRIB OF RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 13.1 | 38 | 48.75 | 4 (installed 2019) | 97.48 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1746
United Utilities | KINGFISHER DRIVE CSO 092BS | Kingfisher Drive CSO | 01BRY0011 | BRY0011 | SO | SO on sewer network | SD8168011790 | GB112069064600 | Roch (Spodden to Irwell) | CLVRTD SECTION GYPSY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.13 | 2 | 9.2 | 5 (installed 2018) | 100 | [5 empty] | UUG1747
United Utilities | WOODHILL ROAD CSO 092JP | Woodhill Road CSO | 01BRY0012 | BRY0012 | SO | SO on sewer network | SD7971011340 | GB112069064610 | Kirklees Brook | WOODHILL BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 3.7 | 3 | 4.2 | 5 (installed 2018) | 99.98 | [5 empty] | UUG1748
United Utilities | RAILWAY STREET CSO | Railway Street CSO | 01BRY0005 | BRY0005 | SO | SO on sewer network | SD7898014681 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 0 | 0 | 8.2857 | 7 (installed 2016) | 100 | [5 empty] | UUG1749
United Utilities | PRIMROSE HILL CSO | Primrose Hill CSO | 01BRY0022 | BRY0022 | SO | SO on sewer network | SD8151010320 | GB112069064600 | Roch (Spodden to Irwell) | BARN BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 150.43 | 32 | 36.1667 | 6 (installed 2017) | 81.91 | Comms failure / issue | Resolved - January after reporting year |  |  |  | UUG1750
United Utilities | BUCKLEY WELLS CSO 091DG | Buckley Wells CSO | 01BRY0023 | BRY0023 | SO | SO on sewer network | SD7947009840 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 229.27 | 68 | 79.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1751
United Utilities | PIMHOLE CSO | Pimhole CSO | 01BRY0021 | BRY0021 | SO | SO on sewer network | SD8147010180 | GB112069064600 | Roch (Spodden to Irwell) | BARN BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 95.87 | 81 | 60.6667 | 6 (installed 2017) | 99.99 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Scheduled | Other investigation - non-WINEP/Green Recovery | UUG1752
United Utilities | REDVALES ROAD CSO | Redvales Road CSO | 01BRY0024 | BRY0024 | SO | SO on sewer network | SD8028008430 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL VIA CULVERT | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1753
United Utilities | LINKSVIEW ESTATE CSO 091BC | Linksview Estate CSO | 01BRY0064 | BRY0064 | SO | SO on sewer network | SD8101007570 | GB112069064600 | Roch (Spodden to Irwell) | PARR BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.2 | 2 | 33.4 | 5 (installed 2018) | 100 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG1754
United Utilities | SUNNY BANK ROAD CSO | Sunny bank Road CSO | 016993479 | BRY0067 | SO | SO on sewer network | SD8082007390 | GB112069064600 | Roch (Spodden to Irwell) | PARR BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 123.64 | 83 | 80.5 | 4 (installed 2019) | 60.59 | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1755
United Utilities | BRIDGE HALL LANE CSO | Bridge Hall Lane CSO | 01BRY0065 | BRY0065 | SO | SO on sewer network | SD8223010640 | GB112069064600 | Roch (Spodden to Irwell) | RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 3.4 | 5 (installed 2018) | 96.65 | [5 empty] | UUG1756
United Utilities | OFF BRANDLESHOLME RD (MH12) CSO | OFF BRANDLESHOLME RD (MH12) CSO | 01BRY0072 | BRY0072 | SO | SO on sewer network | SD7825013500 | GB112069064610 | Kirklees Brook | KIRKLEES BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 135.77 | 49 | 38.4 | 5 (installed 2018) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1757
United Utilities | WATERSIDE MILL CSO | Waterside Mill Combined Sewer Overflow | 016950084 | BRY0081 | SO | SO on sewer network | SD7941009510 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 7.2 | 5 | 5 | 4 (installed 2019) | 100 | [5 empty] | UUG1758
United Utilities | MAPLE AVENUE CSO | Maple Avenue CSO | 01BRY0086 | BRY0086 | SO | SO on sewer network | SD8072004880 | GB112069061451 | Irwell (Croal to Irk) | TRIB BRADLEY BROOK SUF WTR SEW | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 23.2 | 13 | 24.6 | 5 (installed 2018) | 83.83 | Comms failure / issue | Resolved - January after reporting year |  |  |  | UUG1759
United Utilities | TANPITS ROAD CSO | Tanpits Road | 016982617 | BRY0098 | SO | SO on sewer network | SD7973010660 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 243.43 | 72 | 63 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1760
United Utilities | 807 WALMERSLEY ROAD (BURY) CSO | 807 Walmersley Road (Bury) CSO | 016982618 | BRY0116 | SO | SO on sewer network | SD8047013840 | GB112069064620 | Irwell (Rossendale STW to Roch) | WALMERSELY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 3.2 | 7 | 5.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG1761
United Utilities | ROCHDALE ROAD/WASH LANE SSO | Openshaw Park | 016951425 | BRY0126 | SO | SO on sewer network | SD8186010590 | GB112069064600 | Roch (Spodden to Irwell) | RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.83 | 4 | 10.25 | 4 (installed 2019) | 100 | [5 empty] | UUG1762
United Utilities | MANCHESTER ROAD CSO | Manchester Road CSO | 016982936 | BRY0100 | SO | SO on sewer network | SD8070007730 | GB112069061111 | Irwell | The River Roch via a surface water sewer | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.23 | 4 | 5.8 | 5 (installed 2018) | 91.5 | [5 empty] | UUG1763
United Utilities | PARR BROOK CSO | PARR BROOK CSO | 016983249 | BRY0133 | SO | SO on sewer network | SD8157007270 | GB112069064600 | Roch (Spodden to Irwell) | PARR BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 70.84 | 42 | 37.8 | 5 (installed 2018) | 99.98 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1764
United Utilities | OFF WALMERSLEY ROAD CSO 092JL | Off Walmersley Road CSO | 016993850 | BRY0134 | SO | SO on sewer network | SD8062013230 | GB112069064620 | Irwell (Rossendale STW to Roch) | PIGS LEA BROOK TRIB RVR IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 26.57 | 27 | 6.8 | 5 (installed 2018) | 96.84 | [5 empty] | UUG1765
United Utilities | PEEL HALL CSO (BRY0140) | Peel Hall Drive CSO | EPRJB3895AY | BRY0140 | SO | SO on sewer network | SD7890014654 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Not Applicable | Dec 2023 | 667.67 | 154 |  | <1 yr (installed 2023) | 100 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1766
United Utilities | OPP 182 ROCHDALE ROAD CSO (BRY0141) | Opposite 182 Rochdale Road CSO | EPRJB3894EQ | BRY0141 | SO | SO on sewer network | SD8188310641 | GB112069064600 | Roch (Spodden to Irwell) | CLV TRIB OF RIVER ROCH | N/A | N/A | Not Applicable | Dec 2023 | 0.83 | 4 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1767
United Utilities | HOOLEY BRIDGE CSO | Hooley Bridge CSO | 016993763 | ROC0031 | SO | SO on sewer network | SD8544011600 | GB112069064600 | Roch (Spodden to Irwell) | THE RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 465.98 | 87 | 77.25 | 4 (installed 2019) | 56.72 | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1768
United Utilities | WATERFOLD LANE CSO | Waterfold Lane CSO | 01ROC0032 | ROC0032 | SO | SO on sewer network | SD8170010050 | GB112069064600 | Roch (Spodden to Irwell) | RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 640.17 | 117 | 123.5 | 4 (installed 2019) | 100 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1769
United Utilities | MIDDLETON ROAD CSO | Middleton Road (Heywood) CSO | NPSWQD010709 | ROC0033 | SO | SO on sewer network | SD8635009120 | GB112069061250 | Whittle Brook (Irwell) | WHITTLE BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.6 | 4 | 2.5 | 4 (installed 2019) | 99.76 | [5 empty] | UUG1770
United Utilities | JOHN STREET CSO 35020 | John Street CSO | 016993768 | ROC0034 | SO | SO on sewer network | SD8583011010 | GB112069064600 | Roch (Spodden to Irwell) | MILLERS BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 33.46 | 44 | 41 | 5 (installed 2018) | 47.52 | Comms failure / issue | Resolved - Nov | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1771
United Utilities | PEEL LANE CSO NO. 1 | Peel Lane CSO No 1 STORM OVERFLOW | 016993593 | ROC0119 | SO | SO on sewer network | SD8474011330 | GB112069064600 | Roch (Spodden to Irwell) | RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 707.6 | 96 | 78.25 | 4 (installed 2019) | 53.12 | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1772
United Utilities | HEYWOOD (BOTANY STW) CSO | Heywood (Botany STW) CSO | 016950082 | ROC0139 | SO | SO on sewer network | SD8460011500 | GB112069064600 | Roch (Spodden to Irwell) | RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1218.14 | 107 | 88.25 | 4 (installed 2019) | 99.97 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1773
United Utilities | PEEL LANE NO 2 CSO | Peel Lane No. 2 CSO | 01ROC0165 | ROC0165 | SO | SO on sewer network | SD8485011210 | GB112069064600 | Roch (Spodden to Irwell) | RIVER ROCH | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 90.05 | 65 | 65.2 | 5 (installed 2018) | 28.61 | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1774
United Utilities | MIDDLETON RD PS | Middleton Road PS | 016982942 | ROC0184 | SO | Storm discharge at pumping station | SD8638008750 | GB112069061250 | Whittle Brook (Irwell) | WHITTLE BROOK | N/A | N/A | Not Applicable | Commissioned pre-2016 - full year data expected | 17.36 | 3 | 0.375 | 8 (installed 2015) | 100 | [5 empty] | UUG1775
United Utilities | BURTON-IN-LONSDALE STW | BURTON-IN-LONSDALE WwTW | 017260021 | 17260021 | ST | Storm tank at WwTW | SD6495271922 | GB112072071610 | Greta | RIVER GRETA | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 248 | 98 | 136 | 3 (installed 2020) | 99.99 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1776
United Utilities | BURSCOUGH WWTW | BURSCOUGH WwTW | 017030001 | 17030001 | ST | Storm tank at WwTW | SD4249013290 | GB112070064880 | Back Drain and Sluice | BOATHOUSE SLUICE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 329.12 | 25 | 22.2 | 5 (installed 2018) | 100 | [5 empty] | UUG1777
United Utilities | DERBY STREET CSO (49200) | Derby Street CSO | 01WLN0029 | WLN0029 | SO | SO on sewer network | SD4195008880 | GB112070064810 | Eller Brook | TRIB OF ELLER BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 11.26 | 15 | 19.6667 | 3 (installed 2020) | 99.99 | [5 empty] | UUG1778
United Utilities | BURNLEY STW | BURNLEY WwTW | 017160005 | 17160005 | ST | Storm tank at WwTW | SD8285035120 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER (RIBBLE) | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2556.78 | 159 | 135.5 | 4 (installed 2019) | 99.21 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1779
United Utilities | WATERBARN STREET/BARDEN LANE CSO | Waterbarn Street/Barden Lane Combined Sewer Overflow | 017160195 | BUR0003 | SO | SO on sewer network | SD8371034320 | GB112069064660 | Irwell (Source to Whitewell Brook) | UNNAMED TRIB OF RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 2.75 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1780
United Utilities | NE AREA SEWER | Thursby Road/Basnett Street | 017160194 | BUR0002 | SO | SO on sewer network | SD8514033610 | GB112071065100 | Brun - conf Don to conf Calder | RIVER BURN | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1781
United Utilities | PARK ROAD COMBINED SEWER OVERFLOW | Park Road CSO | 01BUR0013 | BUR0013 | SO | SO on sewer network | SD8637030180 | GB112071065060 | Calder - headwaters to conf Brun | RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0.13 | 1 | 2.8333 | 6 (installed 2017) | 100 | [5 empty] | UUG1782
United Utilities | HONEY HOLME LANE CSO | Honey Holme Lane CSO | 01BUR0014 | BUR0014 | SO | SO on sewer network | SD8694029140 | GB112071065060 | Calder - headwaters to conf Brun | RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 334.7 | 85 | 92.5 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1783
United Utilities | Crow Wood Farm CSO | Crow Wood Farm CSO | 17190798 | BUR0016 | SO | SO on sewer network | SD8328033570 | GB112071065120 | Calder - conf Brun to Pendle Water | Calder - conf Brun to Pendle Water | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 508.15 | 123 | 102.6667 | 3 (installed 2020) | 90.09 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1784
United Utilities | BROOKLANDS ROAD/TODMORDEN ROAD CSO | BROOKLANDS ROAD / TODMORDEN ROAD CSO | 01BUR0032 | BUR0032 | SO | SO on sewer network | SD8476031310 | GB112071065060 | Calder - headwaters to conf Brun | UNNAMED TRIB OF RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 4.07 | 14 | 37.25 | 4 (installed 2019) | 100 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG1785
United Utilities | OXFORD RD/HOLLINS ROAD CSO | Oxford Road/Hollins Road CSO | 017190824 | PEN0004 | SO | SO on sewer network | SD8731038750 | GB112071065150 | Colne Water - Wanless Water to Pendle Water | SWINDEN CLOUGH | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 4.67 | 3 | 3.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG1786
United Utilities | 273 REGENT ST CSO (32013) | Rear of 273 Regent Street CSO | 01PEN0006 | PEN0006 | SO | SO on sewer network | SD8681039160 | GB112071065150 | Colne Water - Wanless Water to Pendle Water | SWINDEN CLOUGH | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 225.07 | 40 | 33.6667 | 3 (installed 2020) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1787
United Utilities | CRAWFORD STREET (NELSON) CSO 321P3 | CRAWFORD STREET (Nelson) CSO | 01PEN0008 | PEN0008 | SO | SO on sewer network | SD8620038380 | GB112071065130 | Walverden Water | WALVERDEN WATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 1 | 3 (installed 2020) | 100 | [5 empty] | UUG1788
United Utilities | EDWARD STREET CSO | EDWARD STREET CSO | 01PEN0005 | PEN0005 | SO | SO on sewer network | SD8691039030 | GB112071065150 | Colne Water - Wanless Water to Pendle Water | SWINDEN CLOUGH | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1789
United Utilities | CHAPEL HOUSE ROAD CSO (32014) | Chapel House Road CSO | 01PEN0017 | PEN0017 | SO | SO on sewer network | SD8646037540 | GB112071065130 | Walverden Water | WALVERDEN WATER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 95.9 | 90 | 151.2 | 5 (installed 2018) | 99.96 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1790
United Utilities | BRADLEY ROAD CSO (328N5) | BRADLEY ROAD CSO | 01PEN0010 | PEN0010 | SO | SO on sewer network | SD8619038170 | GB112071065130 | Walverden Water | WALVERDEN WATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 75.33 | Comms failure / issue | Resolved - January after reporting year |  |  |  | UUG1791
United Utilities | SACKVILLE ST MONTAGUE ST CSO | Sackville Street/Montague Street CSO | 01PEN0023 | PEN0023 | SO | SO on sewer network | SD8414036391 | GB112071065490 | Calder - Pendle Water to conf Ribble | PENDLE WATER VIA CULVERT | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0 | 0 | 3.5 | 6 (installed 2017) | 100 | [5 empty] | UUG1792
United Utilities | TIMBER STREET CSO 32021 | Timber Street CSO | 01PEN0022 | PEN0022 | SO | SO on sewer network | SD8466036720 | GB112071065490 | Calder - Pendle Water to conf Ribble | UNNAMED TRIB OF PENDLE WATER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 205.2 | 68 | 76 | 5 (installed 2018) | 83.67 | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1793
United Utilities | LOMESHAYE WAY CSO | Lomeshaye Way CSO | 017180488 | PEN0055 | SO | SO on sewer network | SD8513037900 | GB112071065490 | Calder - Pendle Water to conf Ribble | PENDLE WATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 114.82 | 44 | 33 | 3 (installed 2020) | 98.9 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1794
United Utilities | LINDRED ROAD CSO | Lindred Road CSO | 01PEN0056 | PEN0056 | SO | SO on sewer network | SD8433037340 | GB112071065490 | Calder - Pendle Water to conf Ribble | PENDLE WATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 544.99 | 116 | 135.3333 | 3 (installed 2020) | 98.61 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1795
United Utilities | CLITHEROE ROAD CSO | Clitheroe Road CSO | 017160098 | PEN0058 | SO | SO on sewer network | SD8402036360 | GB112071065490 | Calder - Pendle Water to conf Ribble | PENDLE WATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 997.6 | 147 | 122.3333 | 3 (installed 2020) | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1796
United Utilities | BARROWFORD CSO | Barrowford CSO | 017180569 | PEN0077 | SO | SO on sewer network | SD8530038830 | GB112071065170 | Pendle Water - Colne Water to Walverden Water | PENDLE WATER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 9.37 | 52 | 35.4 | 5 (installed 2018) | 99.95 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1797
United Utilities | 11 NORTH PARK AVENUE CSO | 11 NORTH PARK AVENUE CSO | 01PEN0027 | PEN0027 | SO | SO on sewer network | SD8537038380 | GB112071065490 | Calder - Pendle Water to conf Ribble | PENDLE WATER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 58.65 | 41 | 111 | 4 (installed 2019) | 89.22 | Comms failure / issue | Resolved - January after reporting year | Data collection - EDM non-representative location | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1798
United Utilities | REEDYFORD RD CSO (32020) | Reedyford Road CSO | 017180619 | PEN0080 | SO | SO on sewer network | SD8634038560 | GB112071065130 | Walverden Water | CULVRTD TRIB OF WALVERDEN WTR | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 6.62 | 12 | 10 | 3 (installed 2020) | 99.99 | [5 empty] | UUG1799
United Utilities | FLEET STREET | Fleet Street CSO | 017180622 | PEN0081 | SO | SO on sewer network | SD8600038550 | GB112071065130 | Walverden Water | WALVERDEN WATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 359.87 | 67 | 28.6667 | 3 (installed 2020) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1800
United Utilities | WALVERDEN PARK CSO | Walverden Park CSO | 017180618 | PEN0082 | SO | SO on sewer network | SD8648037530 | GB112071065130 | Walverden Water | WALVERDEN WATER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 59.83 | 21 | 20.5 | 4 (installed 2019) | 99.55 | [5 empty] | UUG1801
United Utilities | NETHERFIELD ROAD CSO (32019) | Netherfield Road CSO | 017180620 | PEN0083 | SO | SO on sewer network | SD8619037550 | GB112071065130 | Walverden Water | WALVERDEN WATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 148.94 | 87 | 68.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1802
United Utilities | CHAPEL HOUSE ROAD (32014) CSO | Chapel House Road CSO(32014) (PEN0084) | 017180623 | PEN0084 | SO | SO on sewer network | SD8646037550 | GB112071065130 | Walverden Water | WALVERDEN WATER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 38.62 | 13 | 30.8 | 5 (installed 2018) | 20 | Comms failure / issue | Resolved - January after reporting year |  |  |  | UUG1803
United Utilities | HEY STREET (PLAYGROUND) CSO (32017) | Hey Street CSO | 017180621 | PEN0085 | SO | SO on sewer network | SD8646038240 | GB112071065130 | Walverden Water | HENDON BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 16.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG1804
United Utilities | 134 BURNLEY ROAD CSO | 134 Burnley Road CSO | 017180606 | PEN0079 | SO | SO on sewer network | SD8668023570 | GB112069064660 | Irwell (Source to Whitewell Brook) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1754.27 | 78 | 19.5 | 4 (installed 2019) | 76.63 | Installation set-up/design issue | N/A - Ongoing investigation | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1805
United Utilities | WARRINGTON/GRAPPENHALL | Grappenhall Resewerage Scheme | 016921094 | WAR0025 | SO | SO on sewer network | SJ6295087000 | 169 |  | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1806
United Utilities | ELLESMERE ROAD CSO 481TI | ELLESMERE ROAD CSO | 01WAR0059 | WAR0059 | SO | SO on sewer network | SJ6128086390 | 169 |  | MANCHESTER SHIP CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.7 | 6 | 10.6 | 5 (installed 2018) | 100 | [5 empty] | UUG1807
United Utilities | BULLGILL WASTEWATER TREATMENT WORKS | BULLGILL WwTW | 017570067 | 17570067 | SO | Inlet SO at WwTW | NY0972038620 | GB112075073640 | Ellen (lower) | RIVER ELLEN | N/A | Allonby | Not Applicable | Commissioned in 2017 - full year data expected | 65.64 | 45 | 68.6667 | 6 (installed 2017) | 99.94 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1808
United Utilities | BULKELEY STW | BULKELEY WwTW | 016810057 | 16810057 | SO | Inlet SO at WwTW | SJ5325055130 | GB112068055300 | Weaver (Source to Marbury Brook) | TRIB RIVER WEAVER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 57.2 | 20 | 30.4 | 5 (installed 2018) | 99.97 | [5 empty] | UUG1809
United Utilities | FOXFIELD SEWAGE PUMPING STATION | Foxfield PS | 017480180 | LAK0097 | SO | Storm discharge at pumping station | SD2096085270 | GB531207411800 | DUDDON | DUDDON ESTUARY | N/A | Askam in Furmess | Not Applicable | Commissioned in 2016 - full year data expected | 298.88 | 27 | 54.7143 | 7 (installed 2016) | 99.88 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1810
United Utilities | DANE BANK ROAD CSO 481QY | Dane Bank Road CSO | 01WAR0068 | WAR0068 | SO | SO on sewer network | SJ6820087520 | 169 |  | SLITTEN BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 219.53 | 85 | 89.2 | 5 (installed 2018) | 99.46 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1811
United Utilities | BROUGH WWTW | BROUGH WwTW | 017670004 | 17670004 | SO | Inlet SO at WwTW | NY7892014180 | GB102076070650 | Swindale Beck Great Musgrave | SWINDALE BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 156.29 | 94 | 189.8 | 5 (installed 2018) | 99.94 |  |  | Performance - Infiltration | Scheduled | Other investigation - non-WINEP/Green Recovery | UUG1812
United Utilities | BROUGH WWTW | BROUGH WwTW | 017670004 | 17670004 | ST | Storm tank at WwTW | NY7892014180 | GB102076070650 | Swindale Beck Great Musgrave | SWINDALE BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1124.73 | 97 | 146.4 | 5 (installed 2018) | 98.51 |  |  | Performance - Infiltration | Scheduled | Other investigation - non-WINEP/Green Recovery | UUG1813
United Utilities | BROOKHOUSE GREEN WASTEWATER WORKS | BROOKHOUSE GREEN WwTW X-X MOSS MERE | 016892175 | 16892175 | SO | Inlet SO at WwTW | SJ8055061340 | GB112068055430 | Arclid Brook | TRIBUTARY OF RIVER WHEELOCK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 23 | 4 | 13.8 | 5 (installed 2018) | 100 | [5 empty] | UUG1814
United Utilities | BROMFIELD WWTW | BROMFIELD WwTW | 017570013 | 17570013 | SO | Inlet SO at WwTW | NY1802047230 | GB102075073480 | Crummock Beck u/s Holme Dub | CRUMMOCK BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1158.36 | 68 | 79.5 | 4 (installed 2019) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1815
United Utilities | WAVERTON PUMPING STATION | Waverton PS | 017580266 | ALL0115 | SO | Storm discharge at pumping station | NY2182047150 | GB102075073440 | Waver | RIVER WAVER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1141.78 | 62 | 80.4 | 5 (installed 2018) | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1816
United Utilities | BLENCOGO PS | Blencogo WwPS | 017580267 | ALL0116 | SO | Storm discharge at pumping station | NY1991048000 | GB102075073440 | Waver | TRIB RIVER WAVER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 29.78 | 17 | 14 | 3 (installed 2020) | 71.99 | Sensor failure / issue | N/A - Ongoing investigation |  |  |  | UUG1817
United Utilities | LANGRIGG PS | Langrigg PS | 017580268 | ALL0117 | SO | Storm discharge at pumping station | NY1728046450 | GB102075073490 | Holme Dub | LANGRIGG BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 38.2 | 15 | 14.3333 | 3 (installed 2020) | 99.62 | [5 empty] | UUG1818
United Utilities | BROMBOROUGH WWTW | BROMBOROUGH WwTW | 016993398 | 16993398 | SO | Inlet SO at WwTW | SJ3471085640 | GB531206908100 | MERSEY | RIVER MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 1241.36 | 144 | 132.1429 | 7 (installed 2016) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1819
United Utilities | BROMBOROUGH WWTW | BROMBOROUGH WwTW | 016993398 | 16993398 | ST | Storm tank at WwTW | SJ3471085640 | GB531206908100 | MERSEY | RIVER MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 2828.6 | 180 | 186 | 7 (installed 2016) | 99.97 |  |  | Data collection - EDM non-representative location | Resolved - January after reporting year | U_INV driver - Stage 4: No cost beneficial solution | UUG1820
United Utilities | HOOTON ROAD CSO 181ZR | HOOTON ROAD CSO | 01ELL0009 | ELL0009 | SO | SO on sewer network | SJ3549078440 | GB112068060270 | Dibbinsdale Brook and Clatter Brook | DIBBINSDALE BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 891.27 | 92 | 76.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1821
United Utilities | WILLASTON RELIEF SEWER | Willaston Relief Sewer | 016810794 | ELL0006 | SO | SO on sewer network | SJ3412078180 | GB112068060270 | Dibbinsdale Brook and Clatter Brook | TRIB DIBBINSDALE BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1822
United Utilities | RR NO 16 BRIDGEWATER ST CSO 483BR | Rear of No. 166 Bridgewater Street CSO | 01WAR0079 | WAR0079 | SO | SO on sewer network | SJ6825087250 | 169 |  | SLITTEN BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 308 | 79 | 70 | 5 (installed 2018) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1823
United Utilities | STANTON ROAD PS | Stanton Road PS | 01WIR0106 | WIR0106 | SO | Storm discharge at pumping station | SJ3244083410 | GB112068060270 | Dibbinsdale Brook and Clatter Brook | BOARDMAN BROOK | N/A | N/A | Not Applicable | Dec 2023 | 15.63 | 2 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1824
United Utilities | SOW BROOK PS | Sow Brook PS | 016982211 | WAR0097 | SO | Storm discharge at pumping station | SJ6823087820 | 169 |  | SOW BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 133.26 | 14 | 14 | 4 (installed 2019) | 98.57 | [5 empty] | UUG1825
United Utilities | REAR OF 68 WHITBARROW RD | Rear of 68 Whitbarrow Road | 016982698 | WAR0106 | SO | SO on sewer network | SJ6751087830 | 169 |  | TRIB M/CHESTER SHIP CANAL | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1826
United Utilities | WINSTON DRIVE HENSINGHAM CSO 02632 | Winston Drive CSO | 017480428 | COP0005 | SO | SO on sewer network | NX9864016940 | 356 |  | SNEBRA BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 9.6 | 11 | 35.4 | 5 (installed 2018) | 99.99 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG1827
United Utilities | EASTHAM RAKE CSO | Eastham Rake Combined Sewer Overflow (Site ID 51068) (WIR0111) | 016892412 | WIR0111 | SO | SO on sewer network | SJ3483079350 | GB112068060270 | Dibbinsdale Brook and Clatter Brook | DIBBINSDALE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 47.34 | 23 | 19 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1828
United Utilities | PORT CAUSEWAY/CROSSWAY CSO | Port Causeway/Crossway CSO | 016881733 | WIR0125 | SO | SO on sewer network | SJ3441083751 | GB112068060270 | Dibbinsdale Brook and Clatter Brook | BROMBOROUGH POOL | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 1.57 | 8 | 51.2857 | 7 (installed 2016) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1829
United Utilities | DOCK ROAD SOUTH CSO | Dock Road South PS, Bromborough | 016810665 | WIR0131 | SO | Storm discharge at pumping station | SJ3541084410 | GB531206908100 | MERSEY | RIVER MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 1623.62 | 158 | 107.5714 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1830
United Utilities | THERMAL ROAD/PORT CAUSEWAY CSO | Thermal Road Port, Causeway | 016881611 | WIR0132 | SO | SO on sewer network | SJ3580083650 | GB531206908100 | MERSEY | THE MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 40 | 49 | 44.5714 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1831
United Utilities | SNEBRA WHITEHAVEN CSO 023B2 | Snebra Whitehaven CSO | 01COP0039 | COP0039 | SO | SO on sewer network | NX9831016730 | 356 |  | TRIB OF POW BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 2.2 | 5 (installed 2018) | 100 | [5 empty] | UUG1832
United Utilities | DOCK ROAD SOUTH CSO | Dock Road South | 016881612 | WIR0134 | SO | SO on sewer network | SJ3541084410 | GB531206908100 | MERSEY | RIVER MERSEY ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 451.03 | 108 | 84.5714 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1833
United Utilities | ESK AVENUE MIREHOUSE CSO | Esk Avenue Mirehouse CSO | 017480429 | COP0041 | SO | SO on sewer network | NX9788017180 | 356 |  | UN-NAMED TRIB OF POW BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 8.75 | 9 | 16.6 | 5 (installed 2018) | 100 | [5 empty] | UUG1834
United Utilities | GRISEDALE CLOSE CSO | Grisedale Close CSO | 017480430 | COP0042 | SO | SO on sewer network | NX9808015940 | 356 |  | POW BECK | N/A | St Bees | Not Applicable | Commissioned in 2016 - full year data expected | 10.63 | 18 | 21.1429 | 7 (installed 2016) | 100 | [5 empty] | UUG1835
United Utilities | CROASDALE AVENUE CSO | CROASDALE AVENUE CSO | 01COP0043 | COP0043 | SO | SO on sewer network | NX9803015940 | 356 |  | POW BECK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 2.1 | 2 | 6.8333 | 6 (installed 2017) | 99.99 | [5 empty] | UUG1836
United Utilities | THORNTON HOUGH PUMPING STATION | Thornton Hough PS | 016892274 | WIR0149 | SO | Storm discharge at pumping station | SJ3071080550 | GB112068060270 | Dibbinsdale Brook and Clatter Brook | THORNTON HOUGH,TRIB OF CLATTER | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 5.91 | 10 | 117.8333 | 6 (installed 2017) | 70.87 | Capital / maintenance works affect EDM operation | Resolved - Dec | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1837
United Utilities | BRIDEKIRK WWTW BRIDE | BRIDEKIRK WwTW | 017570026 | 17570026 | SO | Inlet SO at WwTW | NY1155033800 | GB112075073570 | Broughton Beck | BRIDES BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 94.46 | 26 | 67.4 | 5 (installed 2018) | 92.57 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1838
United Utilities | BRAYSTONES WWTW | BRAYSTONES WwTW | 017470152 | 17470152 | SO | Inlet SO at WwTW | NY0076005070 | GB112074069980 | Ehen (lower) | IRISH SEA | N/A | Seascale | Not Applicable | Commissioned in 2016 - full year data expected | 415.95 | 117 | 164.1429 | 7 (installed 2016) | 99.47 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1839
United Utilities | Bridge End Ind Estate Pumping Station (Site ID 02563) (COP0016) | Bridge End Ind Estate Pumping Station (Site ID 02563) (COP0016) | 017480460 | COP0016 | SO | Storm discharge at pumping station | NY01240999 | GB112074069980 | Ehen (lower) | Ehen (lower) | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 463.86 | 45 | 42 | 4 (installed 2019) | 94.74 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1b: Confirmed "asset maintenance" issue | UUG1840
United Utilities | WYNDHAM TERRACE CSO | Wyndham Terrace CSO | 01COP0028 | COP0028 | SO | SO on sewer network | NY0128011300 | GB112074069980 | Ehen (lower) | RIVER EHEN | N/A | St Bees | Not Applicable | Commissioned in 2016 - full year data expected | 0.73 | 4 | 7.4286 | 7 (installed 2016) | 100 | [5 empty] | UUG1841
United Utilities | POW BRIDGE/STATION ROAD CSO | POW Bridge/Station Road CSO | 017480323 | COP0036 | SO | SO on sewer network | NX9697011980 | GB112068060530 | Pow Beck | POW BECK | N/A | St Bees | Not Applicable | Commissioned in 2016 - full year data expected | 0 | 0 | 1.5714 | 7 (installed 2016) | 100 | [5 empty] | UUG1842
United Utilities | DENT ROAD COMIBINED SEWER OVERFLOW | Dent Road CSO | 01COP0037 | COP0037 | SO | SO on sewer network | NY0075008870 | GB112074069980 | Ehen (lower) | RIVER EHEN | N/A | St Bees | Not Applicable | Commissioned in 2016 - full year data expected | 7.4 | 23 | 26.4286 | 7 (installed 2016) | 100 | [5 empty] | UUG1843
United Utilities | WODOW ROAD COMBINED SEWER OVERFLOW | Wodow Road CSO | 01COP0038 | COP0038 | SO | SO on sewer network | NY0075008871 | GB112074069980 | Ehen (lower) | RIVER EHEN | N/A | St Bees | Not Applicable | Commissioned in 2016 - full year data expected | 0.77 | 5 | 6.5714 | 7 (installed 2016) | 100 | [5 empty] | UUG1844
United Utilities | PICKET HOW FARM SSO | Pickett How Farm CSO | 017470089 | COP0062 | SO | SO on sewer network | NY0117009690 | GB112074069980 | Ehen (lower) | RIVER EHEN | N/A | St Bees | Not Applicable | Commissioned in 2016 - full year data expected | 36.73 | 6 | 10.2857 | 7 (installed 2016) | 100 | [5 empty] | UUG1845
United Utilities | ST BRIDGETS LANE CSO | St Bridgets Lane CSO | 01COP0027 | COP0027 | SO | SO on sewer network | NY0097010620 | GB112074069980 | Ehen (lower) | CULV'T'D SECT OF SKIRTING BECK | N/A | St Bees | Not Applicable | Commissioned in 2016 - full year data expected | 0 | 0 | 0.71429 | 7 (installed 2016) | 96.5 | [5 empty] | UUG1846
United Utilities | ST BEES PUMPING STATION | St Bees PS | 017480322 | COP0097 | SO | SO on sewer network | NX9690011400 | GB112074069990 | Pow Beck (South West Lakes) | POW BECK | N/A | St Bees | Not Applicable | Commissioned in 2017 - full year data expected | 435.74 | 39 | 47.6667 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1847
United Utilities | DEAN VILLAGE WW PUMPING STATION | Dean Ww PS | 017570033 | ALL0102 | SO | Storm discharge at pumping station | NY0665225052 | GB112075070540 | Marron | NEAR STOCK BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1256.35 | 123 | 128.8 | 5 (installed 2018) | 99.9 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1848
United Utilities | BRANTHWAITE PUMPING STATION | Branthwaite PS | 017580264 | ALL0113 | SO | Storm discharge at pumping station | NY0596024930 | GB112075070540 | Marron | RIVER MARRON | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 4.11 | 4 | 7.4 | 5 (installed 2018) | 99.98 | [5 empty] | UUG1849
United Utilities | CUMCATCH / MILTON WEST PS | Cumcatch (Milton West) PS | 017680320 | CAR0075 | SO | Storm discharge at pumping station | NY5479060870 | GB102076074050 | Quarry Beck | MILTON BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 3.58 | 10 | 5 | 4 (installed 2019) | 97.17 | [5 empty] | UUG1850
United Utilities | IRTHINGTON PS | Irthington PS | 017680326 | CAR0081 | SO | Storm discharge at pumping station | NY4992061620 | GB102076073981 | Irthing DS Crammel Linn Waterfall | TRIB RIVER IRTHING | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 15.19 | 5 | 8.5 | 4 (installed 2019) | 99.97 | [5 empty] | UUG1851
United Utilities | MILTON PUMPING STATION | Milton East WW Net PS | 017680328 | CAR0083 | SO | Storm discharge at pumping station | NY5533060550 | GB102076074050 | Quarry Beck | MILTON BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 174.09 | 41 | 29.25 | 4 (installed 2019) | 99.68 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1852
United Utilities | KIRKHOUSE HALLBANKGT PS 10531 | Kirkhouse (Hallbankgate) PS | 017680373 | CAR0094 | SO | Storm discharge at pumping station | NY5651060080 | GB102076074050 | Quarry Beck | MILTON BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 15.07 | 42 | 30 | 5 (installed 2018) | 99.92 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG1853
United Utilities | CSO UPSTREAM OF BRAMPTON WWTW | Brampton CSO (Upstream of Carlisle WwTW) | NPSWQD002928 | CAR0095 | SO | SO on sewer network | NY5087260894 | GB102076073981 | Irthing DS Crammel Linn Waterfall | BRAMPTON BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 11 | 25 | 16.3333 | 3 (installed 2020) | 99.99 | [5 empty] | UUG1854
United Utilities | GELT ROAD CSO | CSO at Gelt Road | 017680282 | CAR0089 | SO | SO on sewer network | NY5260061100 | GB102076073981 | Irthing DS Crammel Linn Waterfall | BRAMPTON BECK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1855
United Utilities | BOWDON WASTEWATER TREATMENT WORKS | BOWDON WwTW | 016940002 | 16940002 | ST | Storm tank at WwTW | SJ7495085600 | GB112069061382 | Bollin (Ashley Mill to Manchester Ship Canal) | RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2517.28 | 157 | 174.5 | 4 (installed 2019) | 100 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1856
United Utilities | POOL BANK FARM BOWDON CSO 452L6 | Pool Bank Farm, Bowdon CSO | 01TRA0053 | TRA0053 | SO | SO on sewer network | SJ7495085601 | GB112069061382 | Bollin (Ashley Mill to Manchester Ship Canal) | RIVER BOLLIN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 425.1 | 114 | 84.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1857
United Utilities | BOTHEL WASTEWATER TREATMENT WORKS | BOTHEL WwTW | 017570066 | 17570066 | SO | Inlet SO at WwTW | NY1825039470 | GB112075073640 | Ellen (lower) | BOTHEL BECK (GILL GOODEN) | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 697.4 | 129 | 176 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1858
United Utilities | GREYHOUND INN CSO 021WR | GREY HOUND INN CSO | 01ALL0015 | ALL0015 | SO | SO on sewer network | NY1833039250 | GB112075073640 | Ellen (lower) | BOTHEL BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 15.5 | 29 | 36 | 5 (installed 2018) | 99.91 | [5 empty] | UUG1859
United Utilities | LATTRIGG RD CSO 022CJ | Lattrigg Road CSO | 017480431 | COP0044 | SO | SO on sewer network | NX9803015660 | 356 |  | CLVRT POW BECK VIA SWS | N/A | St Bees | Not Applicable | Commissioned in 2017 - full year data expected | 9.53 | 9 | 12.5 | 6 (installed 2017) | 100 | [5 empty] | UUG1860
United Utilities | BOOTLE WASTEWATER TREATMENT WORKS | BOOTLE WwTW | 017470043 | 17470043 | ST | Storm tank at WwTW | SD0995088280 | GB112074069720 | Annas | RIVER ANNAS, SYKE BECK | N/A | Silecroft | Not Applicable | Commissioned in 2016 - full year data expected | 150.77 | 30 | 19.2857 | 7 (installed 2016) | 99.91 | [5 empty] | UUG1861
United Utilities | BOLTON PENRITH WWTW | BOLTON (PENRITH) WwTW | 017670002 | 17670002 | SO | Inlet SO at WwTW | NY6428023440 | GB102076070880 | Eden - Scandal Beck to Lyvennet | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 417.56 | 88 | 93 | 5 (installed 2018) | 99.83 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1862
United Utilities | CLIFTON (PENRITH) PUMPING STATION | Clifton PS | 017680335 | EDE0086 | SO | Storm discharge at pumping station | NY5287027380 | GB102076071010 | Lowther (Lower) | TRIB RIVER LOWTHER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 21.25 | 20 | 19.2 | 5 (installed 2018) | 99.8 | [5 empty] | UUG1863
United Utilities | CLIFTON (PENRITH) PUMPING STATION | CLIFTON PS | NPSWQD009945 | EDE0118 | SO | Storm discharge at pumping station | NY5300126548 | GB102076071010 | Lowther (Lower) | RIVER LOWTHER | N/A | N/A | Not Applicable | Dec 2023 | 40.49 | 3 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1864
United Utilities | BOLTON LOW HOUSES STW | BOLTON LOW HOUSES WwTW | 017570012 | 17570012 | ST | Storm tank at WwTW | NY2374044630 | GB102075073440 | Waver | RIVER WAVER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1088.24 | 133 | 124.6667 | 3 (installed 2020) | 99.99 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1865
United Utilities | BOLTON LOW HOUSES CSO | Bolton Low Houses CSO | 017580313 | ALL0014 | SO | SO on sewer network | NY2391044530 | GB102075073440 | Waver | RIVER WAVER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 0.5 | 4 (installed 2019) | 98.24 | [5 empty] | UUG1866
United Utilities | BOLTON WASTEWATER TREATMENT WORKS | BOLTON WwTW | 016950032 | 16950032 | SO | Inlet SO at WwTW | SD7655004690 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 851.06 | 119 | 157.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1867
United Utilities | BOLTON WASTEWATER TREATMENT WORKS | BOLTON WwTW | 016950032 | 16950032 | ST | Storm tank at WwTW | SD7655004690 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1294.05 | 114 | 93.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1868
United Utilities | BROADHEAD ROAD CSO 051FX | BROADHEAD ROAD CSO | 01BBN0019 | BBN0019 | SO | SO on sewer network | SD7433016820 | GB112069064580 | Bradshaw Brook | TRIB QUARLTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 38.73 | 20 | 30.2 | 5 (installed 2018) | 99.99 | [5 empty] | UUG1869
United Utilities | BOLTON ROAD SSO | Bolton Road CSO | 01BBN0133 | BBN0133 | SO | SO on sewer network | SD7418016260 | GB112069064580 | Bradshaw Brook | Bradshaw Brook | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 381.43 | 58 | 57.8 | 5 (installed 2018) | 98.08 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1870
United Utilities | HACKEN WORKS CSO | West of Hacken Works (Syphon) CSO | 016993558 | BOL0013 | SO | SO on sewer network | SD7334007810 | GB112069064550 | Croal (including Blackshaw Brook) | RIVER CROAL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1148.13 | 166 | 148.5 | 4 (installed 2019) | 99.2 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1871
United Utilities | OAKENBOTTOM ROAD CSO 072IS | Oakenbottom Road CSO | 016982221 | BOL0021 | SO | SO on sewer network | SD7355009171 | GB112069064580 | Bradshaw Brook | BRADSHAW BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 3.3 | 8 | 7.8333 | 6 (installed 2017) | 100 | [5 empty] | UUG1872
United Utilities | REGENT ROAD (BOLTON) CSO | Regent Road | EPRQB3499VB | BOL0024 | SO | SO on sewer network | SD6732008590 | GB112069064540 | Middle Brook | BESSY BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 78.8 | 58 | 46.5 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1873
United Utilities | MEADOW RD CSO 023A8 | Meadow Road CSO | 017480432 | COP0045 | SO | SO on sewer network | NX9803015661 | 356 |  | POW BECK | N/A | St Bees | Not Applicable | Commissioned in 2017 - full year data expected | 46.2 | 22 | 23.5 | 6 (installed 2017) | 99.99 | [5 empty] | UUG1874
United Utilities | KEARSLEY PS | Kearsley PS | 016990060 | BOL0036 | SO | Storm discharge at pumping station | SD7568005670 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 396.13 | 88 | 91.8 | 5 (installed 2018) | 90.3 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1875
United Utilities | NO 76 MIDDLE BROOK CSO | No 76 Middle Brook CSO | 01BOL0039 | BOL0039 | SO | SO on sewer network | SD6948008640 | GB112069064540 | Middle Brook | MIDDLE BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 283.47 | 128 | 76 | 6 (installed 2017) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1876
United Utilities | THOMPSON ROAD CSO | Thompson Road Combined Sewer Overflow (Site ID 07055) (BOL0053) | 016950279 | BOL0053 | SO | SO on sewer network | SD6993010450 | GB112069064540 | Middle Brook | CAPTAINS CLOUGH | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 54.5 | 28 | 107.5 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1877
United Utilities | ASTLEY BRIDGE CSO 071WP | Astley Bridge Combined Sewer Overflow (Site ID 071WP) (BOL0056) | 016950340 | BOL0056 | SO | SO on sewer network | SD7152011200 | GB112069064560 | Astley Brook (Irwell) | ASTLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 655.87 | 140 | 139.5 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1878
United Utilities | D/S 56 BARROW BRIDGE ROAD CSO | Downstream of No. 56 Barrow Bridge Road CSO | 016950315 | BOL0055 | SO | SO on sewer network | SD6898011660 | GB112069064560 | Astley Brook (Irwell) | DEAN BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 1.4 | 5 (installed 2018) | 99.92 | [5 empty] | UUG1879
United Utilities | HALL COPPICE SSO | Hall Coppice CSO | 016950415 | BOL0057 | SO | SO on sewer network | SD7085014340 | GB112069064570 | Eagley Brook | EAGLEY BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1880
United Utilities | RIVERSIDE CSO BOLTO BOL0058 | Riverside CSO | 016950464 | BOL0058 | SO | SO on sewer network | SD7633005220 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0.4 | 5 (installed 2018) | 99.92 | [5 empty] | UUG1881
United Utilities | LIGHTBOUNDS RD LVAINE AVE CSO 072CO | LIGHTBOUNDS ROAD / LOUVAINE AVENUE CSO | 01BOL0070 | BOL0070 | SO | SO on sewer network | SD6888011330 | GB112069064560 | Astley Brook (Irwell) | ASTLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0 | 0 | 16 | 6 (installed 2017) | 97.93 | [5 empty] | UUG1882
United Utilities | PLAYFAIR ST | Playfair St/Park Row CSO | 01BOL0069 | BOL0069 | SO | SO on sewer network | SD7175012950 | GB112069064570 | Eagley Brook | EAGLEY BROOK | N/A | N/A | Not Applicable | Dec 2023 | 2 | 6 |  | <1 yr (installed 2023) | 98.5075 | [5 empty] | UUG1883
United Utilities | OLD EAGLEY CSO 073DM | Old Eagley CSO | 016983216 | BOL0073 | SO | SO on sewer network | SD7233012830 | GB112069064570 | Eagley Brook | EAGLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 212.13 | 54 | 53.1667 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1884
United Utilities | HALL I TH WOOD CSO 071XP | HALL i' th WOOD CSO | 01BOL0071 | BOL0071 | SO | SO on sewer network | SD7222011410 | GB112069064570 | Eagley Brook | EAGLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0 | 0 | 2.8333 | 6 (installed 2017) | 96.56 | [5 empty] | UUG1885
United Utilities | ALBION TERRACE CSO 071BD | ALBION TERRACE CSO | 01BOL0075 | BOL0075 | SO | SO on sewer network | SD6969011210 | GB112069064560 | Astley Brook (Irwell) | ASTLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 49.8 | 31 | 60.4 | 5 (installed 2018) | 96.43 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1886
United Utilities | ST JOHNS RD | St Johns Road CSO | 01BOL0074 | BOL0074 | SO | SO on sewer network | SD6697007750 | GB112069064540 | Middle Brook | Middle Brook | N/A | N/A | Not Applicable | Dec 2023 | 26.97 | 28 |  | <1 yr (installed 2023) | 97.64 | [5 empty] | UUG1887
United Utilities | MOSS BANK WAY/CHIPPINGS W | Moss Bank Way/Chippings Road CSO | 01BOL0077 | BOL0077 | SO | SO on sewer network | SD6894010890 | GB112069064560 | Astley Brook (Irwell) | ASTLEY BROOK | N/A | N/A | Not Applicable | Dec 2023 | 827.73 | 146 |  | <1 yr (installed 2023) | 98.5 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1888
United Utilities | TONGE VALLEY CSO | Tonge Valley CSO | 016983223 | BOL0084 | SO | SO on sewer network | SD7208010910 | GB112069064530 | Tonge | RIVER TONGE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0.33333 | 3 (installed 2020) | 100 | [5 empty] | UUG1889
United Utilities | TURNER BRIDGE CSO | Turner Bridge CSO | 016983218 | BOL0092 | SO | SO on sewer network | SD7251009960 | GB112069064530 | Tonge | RIVER TONGE | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 263.92 | 83 | 78.75 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1890
United Utilities | ENTWISTLE ST CSO | Entwistle Street Combined Sewer Overflow (073DQ) (BOL0093) | 016983217 | BOL0093 | SO | SO on sewer network | SD7269009850 | GB112069064530 | Tonge | RIVER TONGE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1488.24 | 64 | 34.4 | 5 (installed 2018) | 38.32 | Comms failure / issue | N/A - Ongoing investigation | Data collection - EDM non-representative location | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1891
United Utilities | ALBERT ROAD CSO | ALBERT ROAD CSO | 01BOL0095 | BOL0095 | SO | SO on sewer network | SD7020008691 | GB112069064540 | Middle Brook | MIDDLE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 6.93 | 28 | 44.75 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1892
United Utilities | CHORLEY NEW ROAD SPS | Chorley New Road/Beaumont Road CSO | 016982073 | BOL0096 | SO | SO on sewer network | SD6440010671 | GB112070064850 | Coral Minor | PEARL BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 46.2 | 41 | 59.8 | 5 (installed 2018) | 99.31 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1893
United Utilities | CHORLEY NEW ROAD CSO 071JS | CHORLEY NEW ROAD CSO | 01BOL0097 | BOL0097 | SO | SO on sewer network | SD6874009330 | GB112069064540 | Middle Brook | TRIB OF MIDDLE BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 40.8 | 49 | 51 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1894
United Utilities | BLACKBURN RD HALLIWELL RD CSO 071EU | Blackburn Road/Halliwell Road CSO | 01BOL0086 | BOL0086 | SO | SO on sewer network | SD7163010290 | GB112069064530 | Tonge | RIVER TONGE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 4.2 | 5 (installed 2018) | 91.1 | [5 empty] | UUG1895
United Utilities | BRIDGE STREET BOW STREET CSO | Bridge Street/Bow Street CSO | 016993547 | BOL0099 | SO | SO on sewer network | SD7171009460 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mers | CVRT SEC MIDDLE BROOK TRIB R R | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 177.54 | 93 | 85 | 5 (installed 2018) | 96.8 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1896
United Utilities | CHORLEY NEW/DEVONSHIRE ROAD CSO | CHORLEY NEW ROAD / DEVONSHIRE ROAD CSO | 01BOL0098 | BOL0098 | SO | SO on sewer network | SD6964009300 | GB112069064540 | Middle Brook | MIDDLE BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1897
United Utilities | BLACKSHAW LANE CSO 072FW | Blackshaw Lane CSO | 01BOL0104 | BOL0104 | SO | SO on sewer network | SD7020008690 | GB112069064540 | Middle Brook | MIDDLE BROOK (RIVER CROAL) | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 11.6 | 21 | 62.8333 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1898
United Utilities | EDITH STREET CSO 078NL | Edith Street CSO | 01BOL0102 | BOL0102 | SO | SO on sewer network | SD7054008870 | GB112069064540 | Middle Brook | RIVER CROAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 1.6 | 5 (installed 2018) | 100 | [5 empty] | UUG1899
United Utilities | HAPATIA STREET CSO 074EA | Hypatia Street CSO | 016983219 | BOL0107 | SO | SO on sewer network | SD7283009350 | GB112069064530 | Tonge | RIVER TONGE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 39.32 | 14 | 44.8 | 5 (installed 2018) | 38.29 | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1900
United Utilities | ZULU SREET CSO 07032 | Zulu Street CSO | 016983222 | BOL0109 | SO | SO on sewer network | SD7288009270 | GB112069064530 | Tonge | RIVER TONGE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 37.31 | 53 | 62.2 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1901
United Utilities | HIND STREET CSO | Hind Street CSO | 016881946 | BOL0110 | SO | SO on sewer network | SD7355009170 | GB112069064580 | Bradshaw Brook | BRADSHAW BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2785.88 | 117 | 26.4 | 5 (installed 2018) | 99.97 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1902
United Utilities | HAG END BROW CSO | Hag End Brow CSO | 016993783 | BOL0111 | SO | SO on sewer network | SD7327008350 | GB112069064530 | Tonge | RIVER TONGE | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 22.63 | 47 | 49.5 | 4 (installed 2019) | 67.66 | Capital / maintenance works affect EDM operation | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1903
United Utilities | DRAGONS TOOTH CSO | Hacken Lane CSO | 016982098 | BOL0114 | SO | SO on sewer network | SD7339007880 | GB112069064550 | Croal (including Blackshaw Brook) | THE RIVER CROAL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 633.38 | 92 | 80.25 | 4 (installed 2019) | 92.05 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1904
United Utilities | WESTON ST VIKING ST CSO BOL0115 | Weston Street/Viking Street CSO | 016983270 | BOL0115 | SO | SO on sewer network | SD7242007900 | GB112069064540 | Middle Brook | JENNY BECK TRIB RVR CROAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 121.85 | 71 | 70.6 | 5 (installed 2018) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1905
United Utilities | 91 MANCHESTER ROAD CSO 072GO | 91 Manchester Road CSO | 01BOL0105 | BOL0105 | SO | SO on sewer network | SD7219008430 | GB112069064540 | Middle Brook | CROAL MINOR | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 357.37 | 108 | 143.2 | 5 (installed 2018) | 50.15 | Sensor failure / issue | Resolved - Jun | Data collection - EDM non-representative location | Resolved - Jun | Other investigation - non-WINEP/Green Recovery | UUG1906
United Utilities | BRIDGEMAN ST HIGHER SWAN LANE CSO | Bridgeman Street/Higher Swan Lane CSO | 01BOL0116 | BOL0116 | SO | SO on sewer network | SD7087007540 | GB112069064540 | Middle Brook | JENNY BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1907
United Utilities | LADYBRIDGE LANE CSO | Ladybridge Lane (Near Ladybridge Brow) CSO | 01BOL0118 | BOL0118 | SO | SO on sewer network | SD6864008920 | GB112069064540 | Middle Brook | MIDDLE BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 80.93 | 43 | 44 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1908
United Utilities | WHITE LION BROW CSO | WHITE LION BROW CSO | 01BOL0119 | BOL0119 | SO | SO on sewer network | SD7123009280 | GB112069064540 | Middle Brook | RIVER CROAL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.33 | 3 | 17.25 | 4 (installed 2019) | 100 | [5 empty] | UUG1909
United Utilities | GISBURN AVENUE CSO 071VO | GISBURN AVENUE CSO | 01BOL0120 | BOL0120 | SO | SO on sewer network | SD6893010900 | GB112069064560 | Astley Brook (Irwell) | ASTLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 28.17 | 27 | 32.6 | 5 (installed 2018) | 99.99 | [5 empty] | UUG1910
United Utilities | CROWN STREET CSO 071QI | CROWN STREET CSO | 01BOL0121 | BOL0121 | SO | SO on sewer network | SD7182009420 | GB112069064540 | Middle Brook | CROAL MINOR | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 97.73 | 102 | 102.2 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1911
United Utilities | MORNINGTON RD BACK LINCOLN RD CSO | Mornington Road/Back Lincoln Road CSO | 01BOL0117 | BOL0117 | SO | SO on sewer network | SD7020709371 | GB112069064540 | Middle Brook | QUEENS PARK GILNOW PARK POND | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.43 | 2 | 5.2 | 5 (installed 2018) | 100 | [5 empty] | UUG1912
United Utilities | MANOR STREET BOW STREET CSO 072ES | MANOR STREET / BOW STREET CSO | 01BOL0122 | BOL0122 | SO | SO on sewer network | SD7187009410 | GB112069064540 | Middle Brook | CROAL MINOR | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.23 | 2 | 1.8 | 5 (installed 2018) | 100 | [5 empty] | UUG1913
United Utilities | ORLANDO STREET CSO 078J3 | Orlando Street CSO | 01BOL0124 | BOL0124 | SO | SO on sewer network | SD7236008520 | GB112069064540 | Middle Brook | CROAL MINOR | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 12.8 | 19 | 22.2 | 5 (installed 2018) | 96.83 | [5 empty] | UUG1914
United Utilities | RISHTON LANE/WESTON STREET CSO | Rishton Lane CSO | 016983269 | BOL0127 | SO | SO on sewer network | SD7182007680 | GB112069064540 | Middle Brook | JENNY BECK, A TRIB OF RV CROAL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 77.41 | 63 | 58.75 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1915
United Utilities | ROYAL OAK CSO 07039 | Royal Oak CSO | 016983304 | BOL0129 | SO | SO on sewer network | SD7347011870 | GB112069064580 | Bradshaw Brook | BRADSHAW BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 1936.35 | 181 | 160 | 6 (installed 2017) | 100 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | U_INV driver - Stage 4: No cost beneficial solution | UUG1916
United Utilities | CHURCH BANK RAILWAY VIADUCT CSO | CHURCH BANK / RAILWAY VIADUCT CSO | 01BOL0130 | BOL0130 | SO | SO on sewer network | SD7214009280 | GB112069064540 | Middle Brook | CROAL MINOR | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0.83 | 7 | 12.6667 | 6 (installed 2017) | 100 | [5 empty] | UUG1917
United Utilities | CHURCH WHARFE CSO 073BW | CHURCH WHARF CSO | 01BOL0131 | BOL0131 | SO | SO on sewer network | SD7215009280 | GB112069064540 | Middle Brook | CLVRT SEC RIVER CROAL MINOR | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 17.57 | 47 | 47.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1918
United Utilities | KING STREET CSO 072BV | KING STREET CSO | 01BOL0123 | BOL0123 | SO | SO on sewer network | SD7138009370 | GB112069064540 | Middle Brook | RIVER CROAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 5.2 | 5 (installed 2018) | 100 | [5 empty] | UUG1919
United Utilities | GINGER FOLD CSO BOL0144 | Ginger Fold CSO | 016993548 | BOL0144 | SO | SO on sewer network | SD7509406798 | GB112069064550 | Croal (including Blackshaw Brook) | RIVER CROAL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 429.68 | 128 | 110.25 | 4 (installed 2019) | 99.91 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1920
United Utilities | HALL LANE | Hall Lane Combined Sewer Overflow (Site ID 07035) (BOL0145) | 01BOL0145 | BOL0145 | SO | SO on sewer network | SD7422006980 | GB112069064550 | Croal (including Blackshaw Brook) | RIVER CROAL | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 13.88 | 26 | 12 | 6 (installed 2017) | 99.99 | [5 empty] | UUG1921
United Utilities | FERN STREET CSO (078J3) | Fern Street CSO | 01BOL0146 | BOL0146 | SO | SO on sewer network | SD7436006851 | GB112069064550 | Croal (including Blackshaw Brook) | RIVER CROAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 3.67 | 15 | 19 | 5 (installed 2018) | 100 | [5 empty] | UUG1922
United Utilities | CAMMERCLOUGH ROAD CSO | Clammerclough CSO | 016993549 | BOL0147 | SO | SO on sewer network | SD7473006060 | GB112069061451 | Irwell (Croal to Irk) | RIVER CROAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 421.68 | 129 | 125.8 | 5 (installed 2018) | 91.9 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1923
United Utilities | HOUGH LANE EAGLEY BRIDGE CSO 073DL | HOUGH LANE/EAGLEY BRIDGE CSO | 01BOL0150 | BOL0150 | SO | SO on sewer network | SD7195013160 | GB112069064570 | Eagley Brook | EAGLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 379.03 | 59 | 51.6 | 5 (installed 2018) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1924
United Utilities | BIRTENSHAW FARM CSO | Birtenshaw Farm CSO (BOL0151) | 016983224 | BOL0151 | SO | SO on sewer network | SD7257012620 | GB112069064570 | Eagley Brook | EAGLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 869.25 | 149 | 128.8 | 5 (installed 2018) | 99.92 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1925
United Utilities | LONGSIGHT PARK CSO 07038 | Longsight Park CSO | 016981480 | BOL0153 | SO | SO on sewer network | SD7344011830 | GB112069064580 | Bradshaw Brook | BRADSHAW BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 751.29 | 153 | 131.6667 | 6 (installed 2017) | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1926
United Utilities | SINGING CLOUGH CSO 071Q8 | Singing Clough CSO | 01BOL0164 | BOL0164 | SO | SO on sewer network | SD7513005210 | GB112069061451 | Irwell (Croal to Irk) | CLVRT TRIB OF RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 23.37 | 23 | 19.8 | 5 (installed 2018) | 99.99 | [5 empty] | UUG1927
United Utilities | DARCY LEVER OLD HALL CSO | Darcy Lever Old Hall CSO | 01BOL0165 | BOL0165 | SO | SO on sewer network | SD7458007770 | GB112069064550 | Croal (including Blackshaw Brook) | BLACKSHAW BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 30.07 | 23 | 22 | 5 (installed 2018) | 97.76 | [5 empty] | UUG1928
United Utilities | SINGING CLOUGH CSO 071Q8 | Singing Clough CSO | 016941213 | BOL0166 | SO | SO on sewer network | SD7533005580 | GB112069061451 | Irwell (Croal to Irk) | CLVRT SINGING CLOUGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 145.74 | 71 | 64 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1929
United Utilities | WATER STREET CSO 07020 | Water Street CSO | 016982191 | BOL0171 | SO | SO on sewer network | SD7205009500 | GB112069064540 | Middle Brook | RIVER CROAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 87.97 | 7 | 3 | 5 (installed 2018) | 55.09 | Comms failure / issue | N/A - Ongoing investigation |  |  |  | UUG1930
United Utilities | SPA ROAD CSO 07017 | Spa Road CSO | 016982192 | BOL0172 | SO | SO on sewer network | SD7070009100 | GB112069064540 | Middle Brook | RIVER CROAL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1008.87 | 81 | 67.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG1931
United Utilities | LADYBRIDGE LANE CSO | Ladybridge Lane CSO | 016982193 | BOL0173 | SO | SO on sewer network | SD6843008910 | GB112069064540 | Middle Brook | MIDDLE BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 29 | 11 | 16.3333 | 3 (installed 2020) | 99.99 | [5 empty] | UUG1932
United Utilities | SHARPLES AVE EASTGROVE AVE CSO 071S | Sharples/East Grove Avenue | 01BOL0134 | BOL0134 | SO | SO on sewer network | SD7154012680 | GB112069064570 | Eagley Brook | EAGLEY BROOK | N/A | N/A | Not Applicable | Dec 2023 | 1425.53 | 227 |  | <1 yr (installed 2023) | 99.5968 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1933
United Utilities | DUNSCAR BRIDGE CSO | Dunscar Bridge CSO (071SU) (BOL0176) | 016982205 | BOL0176 | SO | SO on sewer network | SD7115013430 | GB112069064570 | Eagley Brook | EAGLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1093.6 | 148 | 128.4 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1934
United Utilities | BROOK DEANS CLOSE CSO | Brook Dean Close (Smithhills Dean Road) Combined Sewer Overflow | 016982822 | BOL0179 | SO | SO on sewer network | SD7003011330 | GB112069064560 | Astley Brook (Irwell) | DEAN BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 56.4 | 38 | 21.5 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1935
United Utilities | CHORLEY OLD ROAD SPS | Chorley Old Road/Chorley New Road CSO | 016982075 | BOL0181 | SO | SO on sewer network | SD6819010730 | GB112069064540 | Middle Brook | ASTLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 213.13 | 105 | 99 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1936
United Utilities | STONEHILL ROAD CSO 07049 | Stonehill Road CSO | 016982823 | BOL0182 | SO | SO on sewer network | SD7378404838 | GB112069061451 | Irwell (Croal to Irk) | CULVRT SINGING CLOUGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 69.48 | 42 | 42.4 | 5 (installed 2018) | 79.34 | Comms failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1937
United Utilities | SPRINGFIELD TANK CSO | Springfield Tank CSO | 01BOL0174 | BOL0174 | SO | SO on sewer network | SD7230008930 | GB112069064540 | Middle Brook | RIVER CROAL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 4.33 | 17 | 5.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1938
United Utilities | WALKER STREET CSO | Walker Street | 016982611 | BOL0188 | SO | SO on sewer network | SD7075009090 | GB112069064540 | Middle Brook | RIVER CROAL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 7.83 | 16 | 10 | 3 (installed 2020) | 99.99 | [5 empty] | UUG1939
United Utilities | STONEHILL ROAD CSO 072TV | Stonehill Road CSO | 016982452 | BOL0193 | SO | SO on sewer network | SD7402004820 | GB112069061451 | Irwell (Croal to Irk) | SINGING CLOUGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 180 | 57 | 53.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1940
United Utilities | WATERS MEETING ROAD CSO 073KZ | Waters meeting Road CSO | 016982261 | BOL0197 | SO | SO on sewer network | SD7196011020 | GB112069064530 | Tonge | RIVER TONGE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 139.2 | 65 | 44.6667 | 3 (installed 2020) | 98.38 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1941
United Utilities | CHURCH BANK (SIDE OF VIADUCT) CSO | Church Bank (Side of Viaduct) | 016982610 | BOL0184 | SO | SO on sewer network | SD7214009260 | GB112069064540 | Middle Brook | CROAL MINOR | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1942
United Utilities | CROFT LN MANCHESTER RD CSO BOL0206 | Croft Lane / Manchester Road CSO | 016941054 | BOL0206 | SO | SO on sewer network | SD7249207985 | GB112069064540 | Middle Brook | JENNY BECK CULVERT RIVER CROAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.67 | 4 | 6.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1943
United Utilities | TONGE MOOR RD CSO | Tonge Moor Road CSO | 016982274 | BOL0200 | SO | SO on sewer network | SD7256010000 | GB112069064530 | Tonge | RIVER TONGE | N/A | N/A | Not Applicable | Dec 2023 | 12.13 | 16 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1944
United Utilities | STPETERS WAY/SPRINGFIELD IND ES CSO | St Peters Way/Springfield Industrial Estate CSO | 016982925 | BOL0208 | SO | SO on sewer network | SD7228008811 | GB112069064540 | Middle Brook | RIVER CROAL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 12.3 | 28 | 23.6667 | 3 (installed 2020) | 98.53 | [5 empty] | UUG1945
United Utilities | HOUGH LANE BACK CSO | Hough Lane Back CSO | 016982928 | BOL0207 | SO | SO on sewer network | SD7193013120 | GB112069064570 | Eagley Brook | EAGLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0.2 | 5 (installed 2018) | 99.99 | [5 empty] | UUG1946
United Utilities | VALLETS LANE CSO | Vallets Lane Combined Sewer Overflow (07046) (BOL0227) | 016982920 | BOL0227 | SO | SO on sewer network | SD7015010340 | GB112069064540 | Middle Brook | CLVRT OF CAPTAINS CLOUGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 53.24 | 24 | 24.6 | 5 (installed 2018) | 97.05 | [5 empty] | UUG1947
United Utilities | THICKETFORD CSO 072UX | Thicketford CSO | 016982835 | BOL0229 | SO | SO on sewer network | SD7357010430 | GB112069064580 | Bradshaw Brook | BRADSHAW BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 190.6 | 62 | 38 | 6 (installed 2017) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1948
United Utilities | HEATON BRIDGE CSO BOLTON | Heaton Bridge CSO | 016982883 | BOL0230 | SO | SO on sewer network | SD6791008840 | GB112069064540 | Middle Brook | MIDDLE BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 4.5 | 21 | 20.8 | 5 (installed 2018) | 99.99 | [5 empty] | UUG1949
United Utilities | BRIDGEMAN PARK CSO | Bridgeman Park Combined Sewer Overflow | 016982924 | BOL0209 | SO | SO on sewer network | SD7228008810 | GB112069064540 | Middle Brook | RIVER CROAL | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 2.87 | 8 | 132 | 3 (installed 2020) | 8.3 | Power failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1950
United Utilities | CALEDONIA ST HIBERNIA ST CSO 071IB | Caledonia Street/Hibernia Street CSO | 016982882 | BOL0231 | SO | SO on sewer network | SD7080009120 | GB112069064540 | Middle Brook | MIDDLE BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.07 | 1 | 2.4 | 5 (installed 2018) | 100 | [5 empty] | UUG1951
United Utilities | LEVER STREET NO1 CSO | Lever Street Number 1 CSO | 016983261 | BOL0234 | SO | SO on sewer network | SD7196007831 | GB112069064540 | Middle Brook | A CULVERTED SECTION JENNY BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.43 | 2 | 51.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1952
United Utilities | LEVER STREET NO 3 CSO | Lever Street Number 3 CSO | 016983263 | BOL0236 | SO | SO on sewer network | SD7196007830 | GB112069064540 | Middle Brook | JENNY BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 48.07 | 38 | 38.6 | 5 (installed 2018) | 99.99 | [5 empty] | UUG1953
United Utilities | LEVER STREET NO 5 CSO 078CD | Lever Street Number 5 CSO | 016983265 | BOL0238 | SO | SO on sewer network | SD7196007833 | GB112069064540 | Middle Brook | JENNY BECK A TRIB OF RVR CROAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.4 | 2 | 3.6 | 5 (installed 2018) | 100 | [5 empty] | UUG1954
United Utilities | LOSTOCK JUNCTION LANE CSO | Lostock Junction Lane CSO | 016983108 | BOL0233 | SO | SO on sewer network | SD6732008601 | GB112069064540 | Middle Brook | BESSY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 5 (installed 2018) | 99.99 | [5 empty] | UUG1955
United Utilities | CHURCH STREET WEST CSO | Church Street West CSO | 016993584 | BRY0019 | SO | SO on sewer network | SD7662010460 | GB112069060840 | Irwell (Roch to Croal) | UNNAMED POND | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2.61 | 5 | 3.2 | 5 (installed 2018) | 99.97 | [5 empty] | UUG1956
United Utilities | ST ANDREWS RD BROOKS AV CSO 09001 | Junction of St Andrews Road/Brooks Avenue CSO | 016993585 | BRY0025 | SO | SO on sewer network | SD7786008710 | GB112069060840 | Irwell (Roch to Croal) | BLACK LANE BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 50.17 | 17 | 12.8 | 5 (installed 2018) | 99.99 | [5 empty] | UUG1957
United Utilities | DUMERS LANE PUMPING STATION | Dumers Lane PS | NPSWQD010892 | BRY0026 | SO | Storm discharge at pumping station | SD8003008120 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.31 | 2 | 2.6 | 5 (installed 2018) | 100 | [5 empty] | UUG1958
United Utilities | BOLTON RD CANUTE STREET CSO | Bolton Road/Canute Street CSO | 01BRY0027 | BRY0027 | SO | SO on sewer network | SD7792006830 | GB112069060840 | Irwell (Roch to Croal) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1331.22 | 158 | 124.6 | 5 (installed 2018) | 99.94 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1959
United Utilities | CHURCH STREET WEST CSO 091KB | Church Street West CSO | 01BRY0029 | BRY0029 | SO | SO on sewer network | SD7878007090 | GB112069060840 | Irwell (Roch to Croal) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.97 | 4 | 5.4 | 5 (installed 2018) | 97.5 | [5 empty] | UUG1960
United Utilities | RADCLIFFE CENTRAL CSO | OUTSIDE THE BRIDGE TAVERN CSO | 01BRY0030 | BRY0030 | SO | SO on sewer network | SD7860006950 | GB112069060840 | Irwell (Roch to Croal) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 115.73 | 65 | 64.4 | 5 (installed 2018) | 76.48 | Comms failure / issue | Resolved - January after reporting year | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1961
United Utilities | CHURCH STREET EAST 09003 | Church Street East CSO | 016993586 | BRY0031 | SO | SO on sewer network | SD7909007251 | GB112069060840 | Irwell (Roch to Croal) | UNNAMED TRIB OF RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 369.13 | 43 | 64.6 | 5 (installed 2018) | 99.88 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1962
United Utilities | SION STREET CSO 09026 | Sion Street CSO | 01BRY0032 | BRY0032 | SO | SO on sewer network | SD7795006820 | GB112069060840 | Irwell (Roch to Croal) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2188.24 | 125 | 67.8 | 5 (installed 2018) | 82.64 | Capital / maintenance works affect EDM operation | Resolved - Dec | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1963
United Utilities | LOMAX STREET CSO | Lomax Street combined sewer overflow (099AA) (BRY0033) | 016993829 | BRY0033 | SO | SO on sewer network | SD7845006660 | GB112069060840 | Irwell (Roch to Croal) | THE RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 256.07 | 46 | 94.8 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1964
United Utilities | STAND LANE CSO 09058 | Stand Lane CSO | 01BRY0036 | BRY0036 | SO | SO on sewer network | SD7863006940 | GB112069060840 | Irwell (Roch to Croal) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 904.29 | 145 | 135.2 | 5 (installed 2018) | 97.64 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1965
United Utilities | MOUNT SION ROAD CSO | Mount Sion Road | 01BRY0037 | BRY0037 | SO | SO on sewer network | SD7738006470 | GB112069060840 | Irwell (Roch to Croal) | RIVER IRWELL | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1966
United Utilities | CLIFTON RD LEACH ST CSO 091KQ | Clifton Road/Leach Street CSO | 01BRY0039 | BRY0039 | SO | SO on sewer network | SD8056003980 | GB112069061451 | Irwell (Croal to Irk) | TRIB PRESTWICH CLOUGH VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.83 | 11 | 11.2 | 5 (installed 2018) | 95.81 | [5 empty] | UUG1967
United Utilities | PRESTWICH CLOUGH CSO 09034 | Prestwich Clough CSO | 016983247 | BRY0040 | SO | SO on sewer network | SD8117003530 | GB112069061451 | Irwell (Croal to Irk) | PRESTWICH CLOUGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 31.74 | 23 | 14.2 | 5 (installed 2018) | 97.32 | [5 empty] | UUG1968
United Utilities | HAMPDEN ROAD CSO 091XV | Hampden Road CSO | 016993787 | BRY0041 | SO | SO on sewer network | SD8191003930 | GB112069061451 | Irwell (Croal to Irk) | PRESTWICH CLOUGH VIA CLVRT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 3.53 | 13 | 25.8 | 5 (installed 2018) | 100 | [5 empty] | UUG1969
United Utilities | FARM HILL CSO 091KO | Farm Hill CSO | 01BRY0038 | BRY0038 | SO | SO on sewer network | SD8053003980 | GB112069061451 | Irwell (Croal to Irk) | PRESTWICH CLOUGH VIA CULVERT | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 50.23 | 61 | 12.2 | 5 (installed 2018) | 97.29 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1970
United Utilities | THE CRESCENT CSO 091EJ | The Crescent CSO | 01BRY0043 | BRY0043 | SO | SO on sewer network | SD8174003690 | GB112069061451 | Irwell (Croal to Irk) | PRESTWICH CLOUGH VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.77 | 6 | 7 | 5 (installed 2018) | 98.43 | [5 empty] | UUG1971
United Utilities | CARR CLOUGH CSO 091IG | Carr Clough CSO | 01BRY0044 | BRY0044 | SO | SO on sewer network | SD8034002600 | GB112069061451 | Irwell (Croal to Irk) | PRESTWICH CLOUGH CLVRT IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 50.8 | 74 | 75.2 | 5 (installed 2018) | 97.37 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG1972
United Utilities | HEYWOOD ROAD CSO 091YZ | Heywood Road CSO | 016993905 | BRY0042 | SO | SO on sewer network | SD8191003931 | GB112069061451 | Irwell (Croal to Irk) | CULVERT OF PRESTWICH CLOUGH | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.7 | 6 | 3.8 | 5 (installed 2018) | 100 | [5 empty] | UUG1973
United Utilities | RAINSOUGH BROW CSO | Rainsough Brow CSO | 016983242 | BRY0053 | SO | SO on sewer network | SD8069002040 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 268.02 | 116 | 104 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1974
United Utilities | AGECROFT ROAD EAST CSO | Agecroft Road East CSO | 01BRY0045 | BRY0045 | SO | SO on sewer network | SD8060002130 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL VIA CULVERT | N/A | N/A | Not Applicable | Dec 2023 | 1 | 9 |  | <1 yr (installed 2023) | 98.1982 | [5 empty] | UUG1975
United Utilities | PRESTWICH PS | Prestwich PS | 016983172 | BRY0078 | SO | Storm discharge at pumping station | SD7986003070 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 691.48 | 131 | 116.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG1976
United Utilities | MATHER AVE ALBERT AVE CSO | Mather Avenue/Albert Avenue CSO | 016950319 | BRY0082 | SO | SO on sewer network | SD8218002340 | GB112069061451 | Irwell (Croal to Irk) | SINGLETON BROOK TRIB R IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 7.7 | 20 | 15.8 | 5 (installed 2018) | 100 | [5 empty] | UUG1977
United Utilities | PARK LANE D/S OF S.W. | Park Lane PS | 01BRY0075 | BRY0075 | SO | Storm discharge at pumping station | SD7998004962 | GB112069061451 | Irwell (Croal to Irk) | UNKNOWN | N/A | Fleetwood | Not Applicable | Dec 2023 | 2.05 | 1 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1978
United Utilities | PHILIPS DRIVE (WHITEFIELD) CSO | Phillips Drive (Whitefield) CSO | 016951196 | BRY0127 | SO | SO on sewer network | SD7998004961 | GB112069061451 | Irwell (Croal to Irk) | TRIB BRADLEY BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 319.15 | 65 | 66.5 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1979
United Utilities | RADCLIFFE CENTRAL CSO | Radclife Central CSO | 016982932 | BRY0128 | SO | SO on sewer network | SD7860006950 | GB112069060840 | Irwell (Roch to Croal) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 18.91 | 19 | 27.6 | 5 (installed 2018) | 99.99 | [5 empty] | UUG1980
United Utilities | BURY NEW ROAD CSO | Bury New Road CSO | 016982878 | BRY0130 | SO | SO on sewer network | SD8206002330 | GB112069061451 | Irwell (Croal to Irk) | SINGLETON BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 36.93 | 44 | 50.4 | 5 (installed 2018) | 59.21 | Comms failure / issue | N/A - Ongoing investigation | Performance - Asset power failure | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1981
United Utilities | PRESTWICH GOLF COURSE CSO 093IR | Prestwich Golf Course CSO | 016983241 | BRY0132 | SO | SO on sewer network | SD8150002170 | GB112069061451 | Irwell (Croal to Irk) | SINGLETON BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 13.89 | 17 | 14 | 5 (installed 2018) | 100 | [5 empty] | UUG1982
United Utilities | BURY NEW ROAD CSO | Bury New Road CSO | 016982879 | BRY0131 | SO | SO on sewer network | SD8206002330 | GB112069061451 | Irwell (Croal to Irk) | PRESTWICH CLOUGH BROOK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG1983
United Utilities | MORRIS STREET CSO (BRY0137) | Morris Street CSO | EPRJB3893EY | BRY0137 | SO | SO on sewer network | SD8009308224 | GB112069064620 | Irwell (Rossendale STW to Roch) | RIVER IRWELL | N/A | N/A | Not Applicable | Dec 2023 | 0.07 | 1 |  | <1 yr (installed 2023) | 97.1774 | [5 empty] | UUG1984
United Utilities | ROBIN HOOD CLIFTON PUMPING STATION | Robin Hood (Clifton) PS | 016993828 | SAL0031 | SO | Storm discharge at pumping station | SD7845003556 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 22.8 | 13 | 13.5 | 4 (installed 2019) | 100 | [5 empty] | UUG1985
United Utilities | AGECROFT POWER STATION CSO | Agecroft Power Station | EPRQB3594EP | SAL0097 | SO | SO on sewer network | SD8050002130 | GB112069061451 | Irwell (Croal to Irk) | THE RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 277.9 | 116 | 95.75 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1986
United Utilities | CSO ADJ TO NUMBER 214 RAKE LANE | Rake Lane CSO | 016993808 | SAL0102 | SO | SO on sewer network | SD7915101871 | GB112069061451 | Irwell (Croal to Irk) | SLACK BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 320.78 | 62 | 55.8 | 5 (installed 2018) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1987
United Utilities | CITY WALK PS | Near City Walk | 016940402 | SAL0104 | SO | Storm discharge at pumping station | SD7884002140 | GB112069061451 | Irwell (Croal to Irk) | TRIB SLACK BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 5.66 | 7 | 36.75 | 4 (installed 2019) | 99.99 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG1988
United Utilities | MERE DRIVE / RAKE LANE CSO (374Y5) | Mere Drive/Rake Lane CSO | 016993604 | SAL0109 | SO | SO on sewer network | SD7916001880 | GB112069061451 | Irwell (Croal to Irk) | SLACK BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 173.37 | 47 | 56.3333 | 3 (installed 2020) | 97.86 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1989
United Utilities | CLIFTON HOUSE ROAD PUMPING STATION | Clifton House Road (37010) (SAL0145) | 016940527 | SAL0145 | SO | Storm discharge at pumping station | SD7698004370 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL VIA S.W. | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.83 | 2 | 3.6 | 5 (installed 2018) | 100 | [5 empty] | UUG1990
United Utilities | CLIFTON PUMPING STATION | Clifton PS | 016940035 | SAL0148 | SO | Storm discharge at pumping station | SD8004002540 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 459.78 | 88 | 80.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1991
United Utilities | STONEHILL TRADING ESTATE CSO | Stonehill Trading Estate CSO | 016993835 | SAL0181 | SO | SO on sewer network | SD7401104791 | GB112069061451 | Irwell (Croal to Irk) | SINGING CLOUGH BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 5.25 | 4 (installed 2019) | 100 | [5 empty] | UUG1992
United Utilities | LAMPLIGHT WAY PS | Lamplight Way Pumping Station | 016993416 | SAL0191 | SO | Storm discharge at pumping station | SD8081001050 | GB112069061451 | Irwell (Croal to Irk) | RIVER IRWELL | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.84 | 3 | 19.25 | 4 (installed 2019) | 99.99 | [5 empty] | UUG1993
United Utilities | QUEENSWAY CSO | The Queensway CSO | 016892228 | SAL0193 | SO | SO on sewer network | SD7915001870 | GB112069061451 | Irwell (Croal to Irk) | SLACK BROOK VIA SUFACE WATER S | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 54.45 | 36 | 29 | 5 (installed 2018) | 100 | [5 empty] | UUG1994
United Utilities | BLINDCRAKE WWTW | Blindcrake Wastewater Treatment Works (BLIND) (017570023) | 017570023 | 17570023 | ST | Storm tank at WwTW | NY1494034380 | GB112075073562 | Derwent DS Bassenthwaite Lake | GILL BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 454.82 | 71 | 85.4 | 5 (installed 2018) | 99.72 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1995
United Utilities | BLENNERHASSET WWTW BLENN | BLENNERHASSET WwTW | 017570065 | 17570065 | ST | Storm tank at WwTW | NY1706041460 | GB112075073650 | Ellen (middle) | RIVER ELLEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 4.21 | 1 | 24.8 | 5 (installed 2018) | 100 | [5 empty] | UUG1996
United Utilities | BLENNERHASSET WW PUMPING STATION | Blennerhassett Ww PS | 017570109 | ALL0061 | SO | Storm discharge at pumping station | NY1753041430 | GB112075073650 | Ellen (middle) | RIVER ELLEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 3184.93 | 178 | 221.6 | 5 (installed 2018) | 100 |  |  | Performance - Infiltration | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG1997
United Utilities | BLENCARN WWTW | BLENCARN WwTW | 017670047 | 17670047 | SO | Inlet SO at WwTW | NY6349031480 | GB102076073800 | Briggle Beck | BLENCARN BECK | N/A | N/A | Not Applicable | Dec 2023 | 131.38 | 14 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG1998
United Utilities | BLACKBURN WWTW | BLACKBURN WwTW | 017160024 | 17160024 | ST | Storm tank at WwTW | SD6047029410 | GB112071065300 | Darwen - conf Roddlesworth to tidal | HOLE BROOK & RIVER DARWEN | N/A | Southport; St Annes Pier; St. Annes North; Blackpool South | Not Applicable | Commissioned in 2017 - full year data expected | 193.45 | 29 | 58.6667 | 6 (installed 2017) | 99.98 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG1999
United Utilities | BROWNHILL DRIVE CSO | BROWNHILL DRIVE CSO | 01BBN0013 | BBN0013 | SO | SO on sewer network | SD6948029920 | GB112071065310 | Blakewater | TRIB OF RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.67 | 6 | 8 | 4 (installed 2019) | 100 | [5 empty] | UUG2000
United Utilities | WHALLEY NEW ROAD CSO | WHALLEY NEW ROAD CSO | 01BBN0014 | BBN0014 | SO | SO on sewer network | SD6895029070 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.03 | 1 | 5.25 | 4 (installed 2019) | 100 | [5 empty] | UUG2001
United Utilities | QUEENS PARK ROAD CSO | Queens Park Road CSO | EPRJP3122XY | BBN0016A | SO | SO on sewer network | SD6934827603 | GB112071065310 | Blakewater | QUEENS PARK CULVERT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 104.49 | 48 | 35.75 | 4 (installed 2019) | 98.83 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG2002
United Utilities | CUMBERLAND STREET CSO | Cumberland Street CSO | NPSWQD010680 | BBN0016 | SO | SO on sewer network | SD6887027440 | GB112071065310 | Blakewater | QUEENS PARK CULVERT VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 291.78 | 83 | 74.5 | 4 (installed 2019) | 99.94 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2003
United Utilities | DICKENS STREET CSO | Dickens Street CSO | 01BBN0018 | BBN0018 | SO | SO on sewer network | SD6887027442 | GB112071065310 | Blakewater | QUEENS PARK CULVERT | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 92.98 | 26 | 46.75 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2004
United Utilities | BOLTON ROAD COMBINED SEWER OVERFLOW | Bolton Road CSO | NPSWQD010684 | BBN0023 | SO | SO on sewer network | SD6769026340 | GB112071065240 | Darwen - headwaters to conf Davy Field Bk | UNNAMED TRIB OF RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 19.77 | 22 | 48 | 4 (installed 2019) | 99.19 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG2005
United Utilities | WELLINGTON ROAD CSO | WELLINGTON ROAD CSO | 01BBN0024 | BBN0024 | SO | SO on sewer network | SD6729027040 | GB112071065270 | Darwen - conf Davy Field Bk to conf Blakewater | RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 3.37 | 5 | 4.2 | 5 (installed 2018) | 100 | [5 empty] | UUG2006
United Utilities | PRESTON NEW ROAD | Yew Tree Drive CSO | 017091436 | BBN0026 | SO | SO on sewer network | SD6564029540 | GB112071065300 | Darwen - conf Roddlesworth to tidal | TRIB OF ARLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 624.59 | 62 | 80 | 3 (installed 2020) | 99.89 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG2007
United Utilities | INFIRMARY STREET CSO 05050 | Infirmary Street CSO | 01BBN0027 | BBN0027 | SO | SO on sewer network | SD6789026930 | GB112071065270 | Darwen - conf Davy Field Bk to conf Blakewater | LEEDS/LIVERPOOL CANAL | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 135.8 | 16 | 6.6 | 5 (installed 2018) | 100 | [5 empty] | UUG2008
United Utilities | THWAITES BREWERY YARD | Thwaites Brewery Yard CSO | 01BBN0030 | BBN0030 | SO | SO on sewer network | SD6843028330 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 223.98 | 77 | 60.6667 | 3 (installed 2020) | 99.87 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2009
United Utilities | GATE STREET CSO | GATE STREET CSO | 01BBN0031 | BBN0031 | SO | SO on sewer network | SD6932028230 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 25.33 | 42 | 34.3333 | 3 (installed 2020) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG2010
United Utilities | GREAT BOLTON STREET CSO | Great Bolton Street CSO | 01BBN0025 | BBN0025 | SO | SO on sewer network | SD6806827642 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0 | 0 | 9.5 | 4 (installed 2019) | 99.68 | [5 empty] | UUG2011
United Utilities | BEECHWOOD ROAD CSO | Beechwood Road CSO | EPRBP3624GH | BBN0034 | SO | SO on sewer network | SD6945029050 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.6 | 3 | 13.5 | 4 (installed 2019) | 100 | [5 empty] | UUG2012
United Utilities | GRIMSHAW PARK CSO | Grimshaw Park CSO | 01BBN0037 | BBN0037 | SO | SO on sewer network | SD6854027100 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.37 | 1 | 1 | 4 (installed 2019) | 100 | [5 empty] | UUG2013
United Utilities | DAISY LANE CSO | DAISY LANE CSO | 01BBN0033 | BBN0033 | SO | SO on sewer network | SD6903028610 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Dec 2023 | 1973.87 | 152 |  | <1 yr (installed 2023) | 97.3856 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2014
United Utilities | APPLE STREET CSO | APPLE STREET CSO | 01BBN0040 | BBN0040 | SO | SO on sewer network | SD6709027610 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 100.9 | 35 | 31 | 4 (installed 2019) | 97.88 | [5 empty] | UUG2015
United Utilities | ROLLESTON ROAD CSO | Rolleston Road CSO | 016982802 | BBN0041 | SO | SO on sewer network | SD6682427693 | GB112069060920 | Blakewater | The River Blakewater, a tributary of the River Darwen | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 27.91 | 25 | 22.5 | 4 (installed 2019) | 99.99 | [5 empty] | UUG2016
United Utilities | SHARPLES STREET CSO | SHARPLES STREET CSO | 01BBN0038 | BBN0038 | SO | SO on sewer network | SD6795027160 | GB112071065270 | Darwen - conf Davy Field Bk to conf Blakewater | TRIBUTARY OF RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 828.83 | 206 | 177 | 3 (installed 2020) | 99.73 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2017
United Utilities | 293 PRESTON OLD ROAD CSO (052M0) | Preston Old Road CSO | 01BBN0044 | BBN0044 | SO | SO on sewer network | SD6624026970 | GB112071065270 | Darwen - conf Davy Field Bk to conf Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0 | 0 | 0.66667 | 6 (installed 2017) | 100 | [5 empty] | UUG2018
United Utilities | VICTORIA STREET CSO | VICTORIA STREET CSO | 01BBN0047 | BBN0047 | SO | SO on sewer network | SD6840028400 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 8.37 | 33 | 34.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG2019
United Utilities | WHALLEY RANGE/MILLHAM STREET CSO | WHALLEY RANGE / MILLHAM STREET CSO | 01BBN0048 | BBN0048 | SO | SO on sewer network | SD6862028780 | GB112071065310 | Blakewater | RIVER BLAKEWATER VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.93 | 6 | 7.25 | 4 (installed 2019) | 99.99 | [5 empty] | UUG2020
United Utilities | 293 PRESTON OLD ROAD CSO (052M0) | 293 PRESTON OLD ROAD CSO | 01BBN0045 | BBN0045 | SO | SO on sewer network | SD6624026970 | GB112071065270 | Darwen - conf Davy Field Bk to conf Blakewater | RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.13 | 1 | 0.66667 | 3 (installed 2020) | 100 | [5 empty] | UUG2021
United Utilities | PRINGLE STREET CSO | PRINGLE STREET CSO | 01BBN0054 | BBN0054 | SO | SO on sewer network | SD6939027460 | GB112071065310 | Blakewater | TRIBUTARY OF RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1.2 | 3 | 2.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG2022
United Utilities | WHALLEY RANGE/GRACE STREET CSO | Whalley Range CSO | 01BBN0049 | BBN0049 | SO | SO on sewer network | SD6873028890 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1.63 | 8 | 2 | 4 (installed 2019) | 99.98 | [5 empty] | UUG2023
United Utilities | MERCHANTS LANDING CULVERT ST CSO | Merchants Landing (Culvert Street) CSO | 01BBN0056 | BBN0056 | SO | SO on sewer network | SD6877027450 | GB112071065310 | Blakewater | CULVERT CULVERT ST | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 348 | 23 | 27 | 4 (installed 2019) | 99.99 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG2024
United Utilities | PHILIPS ROAD CSO (052LO) | PHILLIPS ROAD CSO | 01BBN0060 | BBN0060 | SO | SO on sewer network | SD6979029590 | GB112071065310 | Blakewater | TRIB OF RIVER BLAKEWATER V SWS | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 328.5 | 131 | 125 | 3 (installed 2020) | 96.72 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG2025
United Utilities | WHALLEY OLD RD/PROVIDENCE ST CSO | WHALLEY OLD ROAD / PROVIDENCE STREET CSO | 01BBN0061 | BBN0061 | SO | SO on sewer network | SD6940029330 | GB112071065310 | Blakewater | LITTLE HARWOOD BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 87.9 | 89 | 73.75 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG2026
United Utilities | NOTRE DAME GARDENS CSO | NOTRE DAME GARDENS CSO | 01BBN0066 | BBN0066 | SO | SO on sewer network | SD6910028990 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 5.77 | 5 | 2.6667 | 3 (installed 2020) | 97.92 | [5 empty] | UUG2027
United Utilities | BACK QUEENS PARK RD | Back Queen's Park Road CSO | 01BBN0055 | BBN0055 | SO | SO on sewer network | SD6938027420 | GB112071065310 | Blakewater | CULVERT PRINGLE ST | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2028
United Utilities | MANOR ROAD CSO (052ER) | MANOR ROAD CSO | 01BBN0068 | BBN0068 | SO | SO on sewer network | SD6701027830 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.4 | 4 | 3 | 3 (installed 2020) | 100 | [5 empty] | UUG2029
United Utilities | WHALLEY RANGE / WESLEY STREET CSO | Whalley Range/Westley Street CSO | NPSWQD010693 | BBN0067 | SO | SO on sewer network | SD6893029050 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 0 | 3 (installed 2020) | 100 | [5 empty] | UUG2030
United Utilities | CHERRY TREE WORKS SITE | Cherry Tree/Feniscowles CSO | 017190595 | BBN0083 | SO | SO on sewer network | SD6590026282 | GB112071065250 | Roddlesworth | TRIB RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 7.03 | 9 | 6.3333 | 3 (installed 2020) | 100 | [5 empty] | UUG2031
United Utilities | DUKES BROW CSO | Dukes Brow Combined Sewer Overflow (Site ID 051SL) (BBN0069) | 01BBN0069 | BBN0069 | SO | SO on sewer network | SD6730028610 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 14.43 | 20 | 27 | 4 (installed 2019) | 97.18 | [5 empty] | UUG2032
United Utilities | AQUEDUCT ROAD CSO | Aqueduct Road CSO | NPSWQD010749 | BBN0086 | SO | SO on sewer network | SD6764326436 | GB112071065270 | Darwen - conf Davy Field Bk to conf Blakewater | RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 789.64 | 90 | 22.5 | 4 (installed 2019) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2033
United Utilities | WITTON TANKS CSO | Witton Tanks CSO | 017180642 | BBN0089 | SO | SO on sewer network | SD6672027570 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 138.75 | 60 | 52.6667 | 3 (installed 2020) | 99.87 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG2034
United Utilities | ADDISON CLOSE CSO | Addison Close CSO | 017180643 | BBN0099 | SO | SO on sewer network | SD6749027830 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 104.88 | 79 | 75.25 | 4 (installed 2019) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG2035
United Utilities | GORSE ST COMBINED SEWER OVERFLOW | Gorse Street CSO | NPSWQD010750 | BBN0087 | SO | SO on sewer network | SD6988328677 | GB112071065310 | Blakewater | RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 134.06 | 56 | 14 | 4 (installed 2019) | 82.94 | Sensor failure / issue | N/A - Ongoing investigation | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG2036
United Utilities | LARK HILL/BROOKHOUSE LANE CSO | Lark Hill/Brook House Lane CSO | 017180473 | BBN0148 | SO | SO on sewer network | SD6874028700 | GB112071065310 | Blakewater | TRIBUTARY OF RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0 | 0 | 4.3333 | 3 (installed 2020) | 93.88 | [5 empty] | UUG2037
United Utilities | REVIDGE RD/PRESTON NEW RD SSO | Revidge Road/Preston New Road | 017180474 | BBN0149 | SO | SO on sewer network | SD6622028840 | GB112071065300 | Darwen - conf Roddlesworth to tidal | TRIB ARLEY BROOK | N/A | N/A | Not Applicable | Dec 2023 | 7.03 | 10 |  | <1 yr (installed 2023) | 94.5946 | [5 empty] | UUG2038
United Utilities | WATERSIDE CSO 052Z1 | Waterside CSO | 017180721 | BBN0152 | SO | SO on sewer network | SD7156023000 | GB112071065260 | Davyfield Brook | WATERSIDE BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 0 | 5 (installed 2018) | 99.99 | [5 empty] | UUG2039
United Utilities | RAMSGREAVE DRIVE CSO | Ramsgreave Drive CSO | 017180475 | BBN0150 | SO | SO on sewer network | SD6824030760 | GB112071065310 | Blakewater | TRIBUTARY OF RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 0.43 | 3 | 1 | 3 (installed 2020) | 100 | [5 empty] | UUG2040
United Utilities | APPLEBY SREETT CSO | Appleby Street CSO | 017180644 | BBN0156 | SO | SO on sewer network | SD6915028540 | GB112071065310 | Blakewater | TRIB OF RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 527.11 | 94 | 78.5 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG2041
United Utilities | ACCRINGTON ROAD CSO | Accrington Road CSO | 017180645 | BBN0157 | SO | SO on sewer network | SD7110028060 | GB112071065310 | Blakewater | CLVRT'D SECTION KNUZDEN BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 156.23 | 70 | 66.25 | 4 (installed 2019) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG2042
United Utilities | LOWER AUDLEY CSO | Lower Audley Street CSO | 017180646 | BBN0158 | SO | SO on sewer network | SD6847027550 | GB112071065310 | Blakewater | TRIBUTARY OF RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 429.63 | 131 | 60.6667 | 3 (installed 2020) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1b: Confirmed "asset maintenance" issue | UUG2043
United Utilities | PHILIPS ROAD CSO | Philips Road CSO | EPRWP3723KF | BBN0167 | SO | SO on sewer network | SD6952129023 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 738.07 | 72 | 67.6667 | 3 (installed 2020) | 97.15 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG2044
United Utilities | NEW MILL STREET CSO | New Mill Street CSO | EPRWP3723XP | BBN0168 | SO | SO on sewer network | SD6871828831 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 511.79 | 36 | 19 | 3 (installed 2020) | 87.25 | Sensor failure / issue | Resolved - Nov |  |  |  | UUG2045
United Utilities | FIELDEN STREET CSO | Fielden Street CSO | 017180518 | BBN0154 | SO | SO on sewer network | SD6752027800 | GB112071065310 | Blakewater | RIVER BLAKEWATER | N/A | N/A | Not Applicable | Dec 2023 | 3366.1 | 154 |  | <1 yr (installed 2023) | 98.0392 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2046
United Utilities | LODGE BANK PUMPING STN | Lodge Bank PS | 016981230 | CHR0052 | SO | Storm discharge at pumping station | SD6204020410 | GB112070064951 | Yarrow US Big Lodge Water | BRINSCALL BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 146.05 | 25 | 21.5 | 4 (installed 2019) | 100 | [5 empty] | UUG2047
United Utilities | WITHNELL FOLD NETWORK PUMPING STATI | Withnell Fold PS | 01CHR0065 | CHR0065 | SO | Storm discharge at pumping station | SD6130023570 | GB112070064911 | Lostock US Farington Weir | KYLN CLOUGH, TRIB OF R LOSTOCK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2833.72 | 172 | 149.75 | 4 (installed 2019) | 99.99 |  |  | Performance - Infiltration | N/A - Ongoing investigation | U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP or Green Recovery | UUG2048
United Utilities | ABBEY VILLAGE PUMPING STATION | Abbey Village Pumping Station (12001) (CHR0080) | 017180377 | CHR0080 | SO | Storm discharge at pumping station | SD6435022930 | GB112071065250 | Roddlesworth | RIVER RODDLESWORTH | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 381.32 | 53 | 48 | 5 (installed 2018) | 99.96 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2049
United Utilities | LOWER BRUNDHURST FARM CSO | Lower Brundhurst Farm CSO | 017190727 | RIB0006 | SO | SO on sewer network | SD6453030530 | GB112071065500 | Ribble - conf Calder to tidal | TRIB OF MELLOR BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 290.91 | 102 | 86 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG2050
United Utilities | WOOD TOP FARM GRINSAGH | Osbaldeston PS | 01RIB0008 | RIB0008 | SO | Storm discharge at pumping station | SD6428031930 | GB112071065500 | Ribble - conf Calder to tidal | UNNAMED TRIB OF BEZZA BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 280.35 | 18 | 28 | 3 (installed 2020) | 91.82 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG2051
United Utilities | OFF MELLOR BROW | Mellor Brook PS | 01RIB0022 | RIB0022 | SO | Storm discharge at pumping station | SD6415031220 | GB112071065500 | Ribble - conf Calder to tidal | Mellor Brook | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 339.92 | 91 | 62.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG2052
United Utilities | BIRKENHEAD WWTW | BIRKENHEAD WWTW | 16993399 | 16993399 | SO | Inlet SO at WwTW | SJ3282089400 | GB112068060530 | The Birket including Arrowe Brook and Fender | River Birket (Great Culvert - downstream length) | N/A | Moreton; Wallasey | Not Applicable | Commissioned in 2016 - full year data expected | 0 | 0 | 19.2857 | 7 (installed 2016) | 99.99 | [5 empty] | UUG2053
United Utilities | BIRKENHEAD WWTW | BIRKENHEAD WWTW | 16993399 | 16993399 | SO | Inlet SO at WwTW | SJ3282089400 | GB112068060530 | The Birket including Arrowe Brook and Fender | River Birket (Great Culvert -downstream length) / River Mersey Estuary (High Tide) | N/A | Moreton; Wallasey | Not Applicable | Commissioned in 2016 - full year data expected | 236.8 | 62 | 38.7143 | 7 (installed 2016) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2054
United Utilities | BIRKENHEAD WWTW BIRKE | BIRKENHEAD WwTW | 016993399 | 16993399 | ST | Storm tank at WwTW | SJ3292089490 | GB531206908100 | MERSEY | RIVER MERSEY ESTUARY/R.BIRKET | N/A | Moreton; Wallasey | Not Applicable | Commissioned in 2016 - full year data expected | 1950.94 | 150 | 128 | 7 (installed 2016) | 99.94 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG2055
United Utilities | UPTON ROAD CSO 513N8 | Upton Road CSO | 01WIR0004 | WIR0004 | SO | SO on sewer network | SJ2761089731 | GB112068060530 | The Birket including Arrowe Brook and Fender | RIVER FENDER | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 72.33 | 40 | 31.8333 | 6 (installed 2017) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG2056
United Utilities | SANDY LANE CSO | Sandy Lane CSO | 016892357 | WIR0059 | SO | SO on sewer network | SJ2905092111 | GB112068060530 | The Birket including Arrowe Brook and Fender | BIDSTON STREAM | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 101.97 | 78 | 82.2857 | 7 (installed 2016) | 99.95 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG2057
United Utilities | LEASOWE ROAD CSO | Leasowe Road CSO | 016892469 | WIR0060 | SO | SO on sewer network | SJ2905092110 | GB112068060530 | The Birket including Arrowe Brook and Fender | BIDSTON STREAM | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 5.15 | 9 | 121.4286 | 7 (installed 2016) | 89.36 | Sensor failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_IMP4 driver - Stage 4: Potential spill reduction scheme - Not yet on current WINEP/AMP or Green Recovery | UUG2058
United Utilities | WALLACRE ROAD/BEAUFORT DRIVE CSO | Wallacre Road/Beaufort Drive CSO | 016892477 | WIR0061 | SO | SO on sewer network | SJ2916091660 | GB112068060530 | The Birket including Arrowe Brook and Fender | BIDSTON STREAM | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 576.77 | 48 | 10.1429 | 7 (installed 2016) | 99.99 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG2059
United Utilities | BIDSTON BY-PASS CSO | Bidston Bypass CSO | 016892425 | WIR0070 | SO | SO on sewer network | SJ2845090890 | GB112068060530 | The Birket including Arrowe Brook and Fender | THE RIVER BIRKETT | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 43.23 | 23 | 118 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG2060
United Utilities | UPTON STORM TANKS | Upton Storm Tanks | 01WIR0071 | WIR0071 | SO | SO on sewer network | SJ2769089030 | GB112068060530 | The Birket including Arrowe Brook and Fender | RIVER FENDER | N/A | Wallasey | Not Applicable | Commissioned in 2016 - full year data expected | 398.24 | 40 | 71.4286 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG2061
United Utilities | NOCTORUM AVENUE CSO 512IB | Noctorum Avenue CSO | 016892430 | WIR0072 | SO | SO on sewer network | SJ2807087940 | GB112068060530 | The Birket including Arrowe Brook and Fender | THE RIVER FENDER | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 164.17 | 95 | 100.1667 | 6 (installed 2017) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2062
United Utilities | BARNSTON STORM TANK 51070 | Barnston Storm Tanks (51CSO065) | 01WIR0095 | WIR0095 | SO | SO on sewer network | SJ2857084290 | GB112068060530 | The Birket including Arrowe Brook and Fender | PRENTON BROOK | N/A | Moreton | Not Applicable | Commissioned in 2016 - full year data expected | 81.73 | 21 | 19.1429 | 7 (installed 2016) | 100 | [5 empty] | UUG2063
United Utilities | Woodside CSO | Woodside CSO | 16931348 | WIR0116 | SO | SO on sewer network | SJ3298089260 | GB531206908100 | MERSEY | MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 1137.47 | 108 | 68.5714 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2064
United Utilities | STATION RD COMBINED SEWER OVERFLOW | Station Road CSO | 016881580 | WIR0117 | SO | SO on sewer network | SJ2915091650 | GB112071065490 | The Birket | Bidston Stream | N/A | New Brighton | Not Applicable | Commissioned in 2020 - full year data expected | 32.84 | 14 | 15.3333 | 3 (installed 2020) | 99.71 | [5 empty] | UUG2065
United Utilities | REAR OF 25 WHEATFIELD CLOSE CSO | The rear of 25 Wheatfield Close CSO | 016881729 | WIR0121 | SO | SO on sewer network | SJ2761089730 | GB112068060530 | The Birket including Arrowe Brook and Fender | RIVER FENDER | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 426.8 | 84 | 81.3333 | 6 (installed 2017) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG2066
United Utilities | HOYLAKE ROAD/CHAPELHILL CSO | Hoylake Road/Chapelhill Road CSO | 016881732 | WIR0124 | SO | SO on sewer network | SJ2764090310 | GB112068060530 | The Birket including Arrowe Brook and Fender | RIVER FENDER | N/A | Moreton | Not Applicable | Commissioned in 2016 - full year data expected | 97.2 | 41 | 32.5714 | 7 (installed 2016) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG2067
United Utilities | BRISCOE DRIVE CSO 511G9 | Briscoe Drive CSO | 016881734 | WIR0126 | SO | SO on sewer network | SJ2761089840 | GB112068060530 | The Birket including Arrowe Brook and Fender | RIVER FENDER | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 1.53 | 4 | 2.8333 | 6 (installed 2017) | 100 | [5 empty] | UUG2068
United Utilities | PARTON N.F. SHORE PUMPING STATION | Parton PS | 017470154 | COP0048 | SO | Storm discharge at pumping station | NX9773020230 | 356 |  | IRISH SEA | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.87 | 17 | 93.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG2069
United Utilities | STANLEY AVENUE/GREEN LANE CSO | Stanley Green Avenue/Green Lane CSO | 016881737 | WIR0135 | SO | SO on sewer network | SJ2902092720 | GB112068060530 | The Birket including Arrowe Brook and Fender | RIVER BIRKET | N/A | Wallasey | Not Applicable | Commissioned in 2016 - full year data expected | 2.47 | 7 | 12.1429 | 7 (installed 2016) | 100 | [5 empty] | UUG2070
United Utilities | BEECHWOOD AVENUE CSO | Beechwood Avenue CSO | 016982989 | WIR0144 | SO | SO on sewer network | SJ2905092100 | GB112068060530 | The Birket including Arrowe Brook and Fender | BIDSTON STREAM | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 0.33 | 3 | 1.4286 | 7 (installed 2016) | 100 | [5 empty] | UUG2071
United Utilities | RIBTON MOORSIDE CSO | Ribton Moorside CSO | 017480288 | COP0085 | SO | SO on sewer network | NX9854016890 | 356 |  | CULVERTED SEC OF SNEBRA BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 3.8 | 5 (installed 2018) | 100 | [5 empty] | UUG2072
United Utilities | WALLASEY WW PUMPING STATION | Wallasey PS (Transfer PS CSO) | 16983300 | WIR0146 | SO | Storm discharge at pumping station | SJ3262090640 | GB531206908100 | MERSEY | RIVER MERSEY ESTUARY | N/A | West Kirby | Not Applicable | Commissioned in 2018 - full year data expected | 1223.32 | 211 | 231.4 | 5 (installed 2018) | 78.2 | Telemetry or data archiving failure / issue | Resolved - Apr | Data collection - EDM non-representative location | Resolved - January after reporting year | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG2073
United Utilities | WALLASEY WW PUMPING STATION | Wallasey PS (Transfer PS CSO) | 16983300 | WIR0146 | SO | Storm discharge at pumping station | SJ3262090640 | GB531206908100 | MERSEY | RIVER MERSEY ESTUARY | N/A | West Kirby | Not Applicable | Commissioned in 2018 - full year data expected | 573.96 | 88 | 57.2 | 5 (installed 2018) | 66.02 | Installation set-up/design issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG2074
United Utilities | WALLASEY WW PUMPING STATION | Wallasey PS (Transfer PS CSO) | 16983300 | WIR0146 | SO | Storm discharge at pumping station | SJ 3259 9065 | GB531206908100 | MERSEY | RIVER MERSEY ESTUARY | N/A | West Kirby | Not Applicable | Commissioned in 2018 - full year data expected | 3.85 | 3 | 10.8 | 5 (installed 2018) | 70.86 | Comms failure / issue | Resolved - Jun |  |  |  | UUG2075
United Utilities | MARYLAND LANE CSO | Maryland Lane CSO | 016892463 | WIR0148 | SO | SO on sewer network | SJ2477090370 | GB112068060530 | The Birket including Arrowe Brook and Fender | ARROWE BROOK | N/A | Moreton | Not Applicable | Commissioned in 2016 - full year data expected | 0.43 | 2 | 4.8571 | 7 (installed 2016) | 99.99 | [5 empty] | UUG2076
United Utilities | WALLACRE ROAD CSO | Wallacre Road CSO | 016892470 | WIR0151 | SO | SO on sewer network | SJ2914091650 | GB112068060530 | The Birket including Arrowe Brook and Fender | MERSEY ESTUARY | N/A | New Brighton | Not Applicable | Commissioned in 2016 - full year data expected | 48.19 | 40 | 34.1429 | 7 (installed 2016) | 99.99 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG2077
United Utilities | BILLINGTON WWTW | BILLINGTON WwTW | 017160003 | 17160003 | ST | Storm tank at WwTW | SD7160036600 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2375.62 | 157 | 186.25 | 4 (installed 2019) | 99.32 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2078
United Utilities | WEST OF DEWHURST FARM CSO 341RS | West of Dewhurst Farm CSO | 01RIB0016 | RIB0016 | SO | SO on sewer network | SD6850034010 | GB112071065710 | Showley Brook | TRIB OF DINCKLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 92.27 | 59 | 55.6667 | 3 (installed 2020) | 98.07 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2079
United Utilities | PETRE ARMS ROUNDABOUT CSO | Petre Arms Roundabout CSO | 01RIB0017 | RIB0017 | SO | SO on sewer network | SD7090034837 | GB112071065490 | Calder - Pendle Water to conf Ribble | STREAM TRIB BUSHBURN BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0 | 0 | 0 | 6 (installed 2017) | 100 | [5 empty] | UUG2080
United Utilities | WHITTAMS FARM CSO 342XW | Whittams Farm CSO | 01RIB0020 | RIB0020 | SO | SO on sewer network | SD7219035710 | GB112071065490 | Calder - Pendle Water to conf Ribble | UNNAMED TRIBUTARY RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 409.7 | 131 | 138.6667 | 6 (installed 2017) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG2081
United Utilities | LONGWORTH RD/R'WAY VIADUCT | Longworth Road/Railway Viaduct CSO | EPRSB3395WA | RIB0021 | SO | SO on sewer network | SD7278036090 | GB112071065490 | Calder - Pendle Water to conf Ribble | RIVER CALDER | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 271.63 | 73 | 49.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2082
United Utilities | MH 63 EAST END OF COPSTER GREEN CSO | M/H 63 East End of Copster Green CSO | EPRSB3396AJ | RIB0047 | SO | SO on sewer network | SD6815034230 | GB112071065710 | Showley Brook | TRIB OF DINCKLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 734.05 | 112 | 104 | 3 (installed 2020) | 96.05 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2083
United Utilities | SOUTH OF OLD LANGHO RD CSO | South of Old Langho Road CSO | 01RIB0019 | RIB0019 | SO | SO on sewer network | SD7066536133 | GB112071065490 | Calder - Pendle Water to conf Ribble | UNNAMED TRIB OF BUSHBURN BROOK | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 0 | 0 | 0 | 6 (installed 2017) | 100 | [5 empty] | UUG2084
United Utilities | COPSTER GREEN SEWER EJE | Copster Green Sewer Ejector Station | 01RIB0048 | RIB0048 | SO | Storm discharge at pumping station | SD6745034230 | GB112071065710 | Showley Brook | Showley Brook | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2085
United Utilities | BILLINGE SOUTH PS | BILLINGE SOUTH PUMPING STATION | 016920126 | STH0125 | SO | Storm discharge at pumping station | SJ5238099020 | GB112069061230 | Black Brook (Mersey Estuary) | TRIB BLACK BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 3.95 | 21 | 5.25 | 4 (installed 2019) | 100 | [5 empty] | UUG2086
United Utilities | BILLINGE SOUTH PS | BILLINGE SOUTH PUMPING STATION | 016920126 | STH0125 | ST | Storm discharge at pumping station | SJ5238099020 | GB112069061230 | Black Brook (Mersey Estuary) | TRIB BLACK BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 461.11 | 47 | 40.5 | 4 (installed 2019) | 100 |  |  | Data collection - EDM non-representative location | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2087
United Utilities | BIDDULPH WASTEWATER TREATMENT WORKS | BIDDULPH WwTW | 016810052 | 16810052 | SO | Inlet SO at WwTW | SJ8867058860 | GB112068055360 | Biddulph Brook | BIDDULPH BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 253.25 | 101 | 120.4 | 5 (installed 2018) | 88.54 | Sensor failure / issue | Resolved - Jul | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG2088
United Utilities | BIDDULPH WASTEWATER TREATMENT WORKS | BIDDULPH WwTW | 016810052 | 16810052 | ST | Storm tank at WwTW | SJ8867058860 | GB112068055360 | Biddulph Brook | BIDDULPH BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 555.1 | 83 | 53.2 | 5 (installed 2018) | 98.49 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG2089
United Utilities | HALLS ROAD CSO (411XQ) | Halls Road CSO | 016810193 | STA0006 | SO | SO on sewer network | SJ8858058380 | GB112068055360 | Biddulph Brook | GILLOW SHAW, TRIB BIDDULPH BRK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1.07 | 2 | 2 | 3 (installed 2020) | 100 | [5 empty] | UUG2090
United Utilities | O/S 57 WOODHOUSE LANE CSO | O/S 57 WOODHOUSE LANE CSO | 01STA0016 | STA0016 | SO | SO on sewer network | SJ8877059030 | GB112068055360 | Biddulph Brook | TRIB OF BIDDULPH BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 61.37 | 36 | 31.3333 | 3 (installed 2020) | 95.7 | [5 empty] | UUG2091
United Utilities | WEST STREET CSO | West Street CSO | 016881772 | STA0017 | SO | SO on sewer network | SJ8794057120 | GB112068055360 | Biddulph Brook | TRIB OF BIDDULPH BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 25.53 | 21 | 15.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG2092
United Utilities | FORGE MILL PS | Forge Mill PS | 01STA0098 | STA0098 | SO | Storm discharge at pumping station | SJ8879059710 | GB112068055360 | Biddulph Brook | BIDDULPH BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 83.93 | 17 | 17.6667 | 3 (installed 2020) | 100 | [5 empty] | UUG2093
United Utilities | BETLEY WASTE WATER TREATMENT WORKS | BETLEY WwTW | 016810049 | 16810049 | ST | Storm tank at WwTW | SJ7500048200 | GB112068055280 | Wistaston Brook | MERE GUTTER | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 689.57 | 76 | 69 | 4 (installed 2019) | 99.92 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2094
United Utilities | BELMONT WWTW | BELMONT WwTW | 016950031 | 16950031 | SO | Inlet SO at WwTW | SD6833015750 | GB112069064570 | Eagley Brook | EAGLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0 | 0 | 1.2 | 5 (installed 2018) | 38.08 | Comms failure / issue | Resolved - January after reporting year |  |  |  | UUG2095
United Utilities | BASSENTHWAITE WWTW | BASSENTHWAITE WwTW | 017570022 | 17570022 | SO | Inlet SO at WwTW | NY2237032150 | GB112075070530 | Dash Beck | HALLS BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 52.02 | 37 | 45 | 4 (installed 2019) | 99.93 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2096
United Utilities | BARTON WASTE WATER TREATMENT WORKS | BARTON WwTW | 017260043 | 17260043 | ST | Storm tank at WwTW | SD5147035720 | GB112072065800 | Barton (Westfield) Brook | BARTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 3140.43 | 188 | 155.6667 | 3 (installed 2020) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2097
United Utilities | GARSTANG ROAD/BILSBORROW PS | Garstang Road, Bilsborrow PS | 017280326 | WYR0009 | SO | Storm discharge at pumping station | SD5095039680 | GB112072065790 | New Draught Brook | BACCHUS BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 183.67 | 20 | 35 | 5 (installed 2018) | 100 | [5 empty] | UUG2098
United Utilities | BARROWNOOK WWTW | BARROW NOOK WwTW | 016930106 | 16930106 | SO | Inlet SO at WwTW | SD4393001440 | GB112069060630 | Simonswood Brook | SIMONSWOOD BROOK | N/A | N/A | Not Applicable | Dec 2023 | 674.38 | 104 |  | <1 yr (installed 2023) | 99.78 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2099
United Utilities | WEST STRAND PUMPING STATION | West Strand pumping station (WSTST) (COP0094) | 017470158 | COP0094 | SO | Storm discharge at pumping station | NX9630018070 | 356 |  | IRISH SEA | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 17.39 | 17 | 75.6 | 5 (installed 2018) | 100 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Stage 1b: Confirmed "asset maintenance" issue | UUG2100
United Utilities | WIDNES WWTW | WIDNES WwTW | 016983012 | 16983012 | ST | Storm tank at WwTW | SJ4851082920 | 167 |  | RIVER MERSEY ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2046.35 | 165 | 203 | 4 (installed 2019) | 100 |  |  | Performance - Other maintenance / capital works (e.g. jetting) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2101
United Utilities | EVERITE ROAD CSO | Everite Road Combined Sewer Overflow (Site ID 20046) (HAL0004) | 016921103 | HAL0004 | SO | SO on sewer network | SJ4890485299 | 167 |  | DITTON BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 112 | 54 | 59.75 | 4 (installed 2019) | 99.73 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2102
United Utilities | ALEXANDER DRIVE CSO | Alexander Drive CSO | 016920990 | HAL0005 | SO | SO on sewer network | SJ4981085330 | 170 |  | STEWARDS BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 215.5 | 76 | 80.25 | 4 (installed 2019) | 95.63 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG2103
United Utilities | DERBY RD BARROWS LANE CSO 203DC | Derby Road/Barrows Green Lane | 016920641 | HAL0038 | SO | SO on sewer network | SJ5355087980 | 170 |  | BARROWS GREEN BROOK SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.43 | 2 | 30.4 | 5 (installed 2018) | 100 | [5 empty] | UUG2104
United Utilities | HARRISON STREET CSO | Harrison Street CSO | 016993466 | HAL0040 | SO | SO on sewer network | SJ4895084630 | 167 |  | DITTON BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 234.77 | 70 | 60.75 | 4 (installed 2019) | 99.57 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2105
United Utilities | DANS ROAD WEATES CLOSE CSO 201Q2 | Dans Road/Weates Close | 01HAL0041 | HAL0041 | SO | SO on sewer network | SJ5395085220 | 170 |  | RIVER MERSEY VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 109.87 | 47 | 40.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2106
United Utilities | HAWCOAT LANE/HARTLAND ROAD CSO | Hawcoat Lane/Hartland Road CSO | 01BRW0031 | BRW0031 | SO | SO on sewer network | SD2194069336 | GB112074069790 | Mill Beck (Poaka Beck) | ROOSE BROOK/MILLBECK | 116 Walney | Walney Biggar Bank; Walney West Shore; Walney Sandy Gap | Not Applicable |  |  |  | 9.5 | 6 (installed 2017) |  | No longer operational as an overflow - permit revoked or to be revoked | Overflow no longer spilling to environment - from Jan |  |  |  | UUG2107
United Utilities | HAWCOAT LANE/THORNCLIFFE ROAD CSO | Hawcoat Lane/Thorncliffe Road CSO | 01BRW0032 | BRW0032 | SO | SO on sewer network | SD2194069337 | GB112074069790 | Mill Beck (Poaka Beck) | ROOSE BROOK/MILLBECK | 116 Walney | Walney Biggar Bank; Walney West Shore; Walney Sandy Gap | Not Applicable |  |  |  | 28 | 6 (installed 2017) |  | No longer operational as an overflow - permit revoked or to be revoked | Overflow no longer spilling to environment - from Jan |  |  |  | UUG2108
United Utilities | ABBEY RD/HOLLOW LANE CSO | Abbey Road/Hollow Lane CSO | 017480443 | BRW0034 | SO | SO on sewer network | SD2194069332 | GB112074069790 | Mill Beck (Poaka Beck) | MILLBECK | 116 Walney | Walney West Shore | Not Applicable | Commissioned in 2016 - full year data expected | 780.23 | 163 | 184.1429 | 7 (installed 2016) | 66.63 | Comms failure / issue | Resolved - January after reporting year | Data collection - EDM non-representative location | Resolved - January after reporting year | Stage 1c: Confirmed "hydraulic issue" | UUG2109
United Utilities | THORNCLIFFE RD/CLIFF LN CSO | Thorncliff Road/Cliff Lane CSO | 017480405 | BRW0033 | SO | SO on sewer network | SD2194069340 | GB112074069790 | Mill Beck (Poaka Beck) | MILL BECK | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2110
United Utilities | DANE AVENUE/WHEATCLOSE ROAD CSO | Dane Avenue/Wheatclose Road CSO | 01BRW0035 | BRW0035 | SO | SO on sewer network | SD2194069334 | GB112074069790 | Mill Beck (Poaka Beck) | ROOSE BROOK/MILLBECK | 116 Walney | Walney West Shore | Not Applicable |  |  |  | 12.8333 | 6 (installed 2017) |  | No longer operational as an overflow - permit revoked or to be revoked | Overflow no longer spilling to environment - from Jan |  |  |  | UUG2111
United Utilities | HOLLOW LANE/OLD HARREL LANE CSO | Hollow Lane/Harrel Lane CSO | 01BRW0036 | BRW0036 | SO | SO on sewer network | SD2194069338 | GB112074069790 | Mill Beck (Poaka Beck) | MILL BECK VIA ROOSE BRIDGE | 116 Walney | Walney Biggar Bank; Walney West Shore; Walney Sandy Gap | Not Applicable |  |  |  | 113.5 | 6 (installed 2017) |  | No longer operational as an overflow - permit revoked or to be revoked | Overflow no longer spilling to environment - from Jan | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2112
United Utilities | RATING LANE/MEADOWLANDS AVENUE CSO | Rating Lane/Meadowlands Avenue CSO | 01BRW0037 | BRW0037 | SO | SO on sewer network | SD2194069339 | GB112074069790 | Mill Beck (Poaka Beck) | ROOSE BRIDGE/MILLBECK | N/A | Walney West Shore | Not Applicable |  |  |  | 13.1429 | 7 (installed 2016) |  | No longer operational as an overflow - permit revoked or to be revoked | Overflow no longer spilling to environment - from Jan |  |  |  | UUG2113
United Utilities | 188 RATING LANE CSO | 188 Rating Lane CSO | 017480404 | BRW0038 | SO | SO on sewer network | SD2194069330 | GB112074069790 | Mill Beck (Poaka Beck) | ROOSE BRIDGE/MILLBECK | N/A | Walney West Shore | Not Applicable |  |  |  | 3 | 7 (installed 2016) |  | No longer operational as an overflow - permit revoked or to be revoked | Overflow no longer spilling to environment - from Jan |  |  |  | UUG2114
United Utilities | 31 ABBOTSMEAD APPROACH CSO | 31 Abbotsmead Approach CSO | 017480449 | BRW0040 | SO | SO on sewer network | SD2177069780 | GB112074069790 | Mill Beck (Poaka Beck) | MILLBECK | N/A | N/A | Not Applicable | Commissioned in 2016 - full year data expected | 13.47 | 26 | 21.7143 | 7 (installed 2016) | 99.99 | [5 empty] | UUG2115
United Utilities | FLASS LANE AT BRIDGEGATE CSO | Flass Lane at Bridgegate Ave, Newbarns CSO (04531/04CSO009) | 01BRW0039 | BRW0039 | SO | SO on sewer network | SD2194069335 | GB112074069790 | Mill Beck (Poaka Beck) | ROOSE BROOK/MILLBECK | 116 Walney | Walney Sandy Gap | Not Applicable |  |  |  | 31.3333 | 6 (installed 2017) |  | No longer operational as an overflow - permit revoked or to be revoked | Overflow no longer spilling to environment - from Jan |  |  |  | UUG2116
United Utilities | BRIDGEGATE AVENUE MANHOLE 5800 CSO | Bridgegate Avenue (manhole 5800) CSO | 01BRW0041 | BRW0041 | SO | SO on sewer network | SD2194069333 | GB112074069790 | Mill Beck (Poaka Beck) | ROOSEBRIDGE/MILLBECK | 116 Walney | Walney Sandy Gap | Not Applicable |  |  |  | 41.8333 | 6 (installed 2017) |  | No longer operational as an overflow - permit revoked or to be revoked | Overflow no longer spilling to environment - from Jan | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2117
United Utilities | GORSEY LANE DANS RD CSO 201V6 | Gorsey Lane/Dan's Road | 01HAL0042 | HAL0042 | SO | SO on sewer network | SJ5395085223 | 170 |  | RIVER MERSEY VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 164.97 | 107 | 108.4 | 5 (installed 2018) | 99.19 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2118
United Utilities | FRENCH STREET CSO 201UW | French Street CSO | 01HAL0043 | HAL0043 | SO | SO on sewer network | SJ5395085222 | 170 |  | RIVER MERSEY VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 222.5 | 67 | 66.3333 | 6 (installed 2017) | 99.72 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG2119
United Utilities | LINDAL PUMPING STATION 04509 | Lindal PS | 017370050 | BRW0072 | SO | Storm discharge at pumping station | SD2471075510 | GB112073071150 | Deep Meadows Beck | TRIB OF CLARKES BECK | N/A | Haverigg | Not Applicable | Commissioned in 2016 - full year data expected | 117.61 | 82 | 86.2857 | 7 (installed 2016) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG2120
United Utilities | 27/29 ABBOTSMEAD CSO | 27/29 Abbotsmead Approach CSO | 17480451 | BRW0042 | SO | SO on sewer network | SD2194069331 | GB112074069790 | Mill Beck (Poaka Beck) | MILL BECK | 116 Walney | Walney Sandy Gap | Not Applicable |  |  |  | 92 | 7 (installed 2016) |  | No longer operational as an overflow - permit revoked or to be revoked | Overflow no longer spilling to environment - from Jan | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2121
United Utilities | DALTON SCREENS CSO | Dalton Screens | 017470006 | BRW0074 | SO | SO on sewer network | SD2232073490 | GB112074069790 | Mill Beck (Poaka Beck) | POAKA BECK | N/A | Walney West Shore | Not Applicable | Commissioned in 2016 - full year data expected | 152.62 | 77 | 57 | 7 (installed 2016) | 93.19 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2122
United Utilities | DESOTO ROAD CSO (201RQ) | DESOTO ROAD CSO | 01HAL0045 | HAL0045 | SO | SO on sewer network | SJ5039083990 | 170 |  | RIVER MERSEY | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 668.77 | 78 | 52 | 3 (installed 2020) | 97.37 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2123
United Utilities | WARRINGTON ROAD CSO | WARRINGTON ROAD CSO | 01HAL0054 | HAL0054 | SO | SO on sewer network | SJ5205084650 | 170 |  | BOWERS BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 40.1 | 33 | 39.2 | 5 (installed 2018) | 95.84 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG2124
United Utilities | PALACE NOOK SEWAGE PUMPING STATION | Palace Nook Sewage Pumping Station (Site ID04522) (BRW0097) | 017480314 | BRW0097 | SO | Storm discharge at pumping station | SD1887071800 | GB641211172000 | Duddon Sands | WALNEY CHANNEL | 116 Walney | Walney Biggar Bank; Walney West Shore; Walney Sandy Gap | Not Applicable | Commissioned in 2017 - full year data expected | 900.98 | 90 | 56.8333 | 6 (installed 2017) | 94.21 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG2125
United Utilities | MACDERMOTT ROAD PUMPING STATION | MacDermott Road Pumping Station (formerly Dock Street PS) | 016980998 | HAL0111 | SO | Storm discharge at pumping station | SJ5091083850 | 341 |  | RIVER MERSEY ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 475.01 | 31 | 15.5 | 4 (installed 2019) | 87.9 | Capital / maintenance works affect EDM operation | Resolved - Dec |  |  |  | UUG2126
United Utilities | ESTER STREET CAR PARK CSO 203DR | Ester Street Car Park CSO | 016982703 | HAL0117 | SO | SO on sewer network | SJ5214086050 | 170 |  | BOWERS BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 44.93 | 38 | 28 | 5 (installed 2018) | 100 | [5 empty] | UUG2127
United Utilities | MERSEY VIEW ROAD CSO | Pickering Pasture SSO | EPRQB3792VW | HAL0118 | SO | SO on sewer network | SJ4888083420 | 167 |  | THE MERSEY ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 346.7 | 87 | 82.5 | 4 (installed 2019) | 95.33 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG2128
United Utilities | ROMNEY ROAD/TITCHFIELD STREET CSO | Romney Road/Titchfield Street CSO | 017480303 | BRW0088 | SO | SO on sewer network | SD1966070554 | GB112069061452 | Ormsgill Reservoir | CROFTS BANK BROOK | N/A | Walney West Shore | Not Applicable | Commissioned in 2016 - full year data expected | 69.03 | 14 | 10.8571 | 7 (installed 2016) | 95.84 | [5 empty] | UUG2129
United Utilities | BARNOLDSWICK WWTW | BARNOLDSWICK WwTW | 017160028 | 17160028 | ST | Storm tank at WwTW | SD8785048010 | GB112071065540 | Stock Beck | STOCK BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 412.92 | 40 | 35.25 | 4 (installed 2019) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG2130
United Utilities | CORNMILL COTTAGES CSO | Cornmill Cottages CSO | 01PEN0021 | PEN0021 | SO | SO on sewer network | SD8778047180 | GB112071065540 | Stock Beck | BUTTS BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.1 | 1 | 2 | 4 (installed 2019) | 100 | [5 empty] | UUG2131
United Utilities | CALF HALL ROAD CSO | Calf Hall Road CSO | 017190815 | PEN0024 | SO | SO on sewer network | SD8746046640 | GB112071065540 | Stock Beck | CALF HALL BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 0.07 | 1 | 5.25 | 4 (installed 2019) | 100 | [5 empty] | UUG2132
United Utilities | NEAR BUTTS BECK CSO (321H7) | Near Butts Beck Footpath CSO | 01PEN0025 | PEN0025 | SO | SO on sewer network | SD8756046820 | GB112071065540 | Stock Beck | BUTTS BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 2.67 | 10 | 9 | 3 (installed 2020) | 95.29 | [5 empty] | UUG2133
United Utilities | DAM HEAD BRIDGE /GISBURN ROAD CSO | Dam Head Bridge CSO | 01PEN0026 | PEN0026 | SO | SO on sewer network | SD8763047040 | GB112071065540 | Stock Beck | BUTTS BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 2.8 | 13 | 12.75 | 4 (installed 2019) | 99.98 | [5 empty] | UUG2134
United Utilities | AUDLEY WASTEWATER TREATMENT WORKS | AUDLEY WwTW | 016810045 | 16810045 | SO | Inlet SO at WwTW | SJ7953051750 | GB112068074630 | Valley Brook (Source to Englesea Brook) | AUDLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 621.32 | 64 | 78.4 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2135
United Utilities | AUDLEY WASTEWATER TREATMENT WORKS | AUDLEY WwTW | 016810045 | 16810045 | ST | Storm tank at WwTW | SJ7953051750 | GB112068074630 | Valley Brook (Source to Englesea Brook) | AUDLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 271.42 | 62 | 78 | 5 (installed 2018) | 99.82 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2136
United Utilities | ALSAGER RD CSO | Alsager Road Combined Sewer Overflow (Site ID 291BO) (NEW0039) | 016882294 | NEW0039 | SO | SO on sewer network | SJ7960051530 | GB112068074630 | Valley Brook (Source to Englesea Brook) | AUDLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 14.33 | 9 | 11.75 | 4 (installed 2019) | 100 | [5 empty] | UUG2137
United Utilities | VICARAGE ROAD CSO | Vicarage Road CSO | 016881768 | CRE0075 | SO | SO on sewer network | SJ6612043510 | GB112068055190 | Audlem Brook | SWANBACK MILL BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 59.33 | 35 | 35.5 | 4 (installed 2019) | 99.98 | [5 empty] | UUG2138
United Utilities | ASPATRIA WASTEWATER TREATMENT WORKS | ASPATRIA WwTW | 017570063 | 17570063 | ST | Storm tank at WwTW | NY1312040280 | GB112075073640 | Ellen (lower) | RIVER ELLEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1298.53 | 104 | 100.2 | 5 (installed 2018) | 99.95 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Stage 1c: Confirmed "hydraulic issue" | UUG2139
United Utilities | NORTH ROAD COMBINED SEWER OVERFLOW | NORTH ROAD CSO | 01ALL0011 | ALL0011 | SO | SO on sewer network | NY1504042270 | GB112075073660 | Crookhurst Beck | UNNAMED TRIB OF SANDWITH BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 3.03 | 12 | 18 | 5 (installed 2018) | 100 | [5 empty] | UUG2140
United Utilities | WHITE HORSE YARD CSO 022X9 | White Horse Yard CSO | 01ALL0028 | ALL0028 | SO | SO on sewer network | NY1414041070 | GB112075073640 | Ellen (lower) | TO RAILWAY TRACK DRAIN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 9.4 | 24 | 33.2 | 5 (installed 2018) | 96.98 | [5 empty] | UUG2141
United Utilities | ELLEN VALE CSO | Ellen Vale | 017580250 | ALL0093 | SO | SO on sewer network | NY1490040800 | GB112075073640 | Ellen (lower) | RIVER ELLEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 228.33 | 84 | 97.6 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG2142
United Utilities | ASKHAM WASTEWATER TREATMENT WORKS | Askham Wastewater Treatment Works (ASKHM) (017670078) | 017670078 | 17670078 | ST | Storm tank at WwTW | NY5183023670 | GB102076071010 | Lowther (Lower) | RIVER LOWTHER | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 414.37 | 47 | 67.2 | 5 (installed 2018) | 94.55 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2143
United Utilities | PUNCH BOWL HOTEL (ASKHAM) CSO | Punch Bowl Hotel (Askham) CSO | 01EDE0008 | EDE0008 | SO | SO on sewer network | NY5159023780 | GB102076071010 | Lowther (Lower) | ASKHAM BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 54.2 | 23 | 14.6667 | 3 (installed 2020) | 99.5 | [5 empty] | UUG2144
United Utilities | WORKINGTON WWTW | WORKINGTON WwTW | 017580285 | 17580285 | SO | Inlet SO at WwTW | NY0048031840 | 357 |  | IRISH SEA | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 991.52 | 157 | 142.6667 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2145
United Utilities | LOWCA LANE HAZEL GROVE CSO | Lowca Lane(Hazel Grove) CSO | 017560139 | ALL0068 | SO | SO on sewer network | NY0119030880 | 188 |  | LING BECK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 443.47 | 89 | 71.25 | 4 (installed 2019) | 94.78 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2146
United Utilities | MELBOURNE TERRACE CSO | Melbourne Terrace CSO | 01ALL0089 | ALL0089 | SO | SO on sewer network | NX9957025470 | 356 |  | UNNAMED TRIB OF RIVER WYRE | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 2.73 | 15 | 29.2 | 5 (installed 2018) | 100 | [5 empty] | UUG2147
United Utilities | ASHTON-UNDER-LYNE STW | ASHTON-UNDER-LYNE WwTW | 016940085 | 16940085 | SO | Inlet SO at WwTW | SJ9300097140 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 815.24 | 63 | 48 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2148
United Utilities | ASHTON-UNDER-LYNE STW | ASHTON-UNDER-LYNE WwTW | 016940085 | 16940085 | ST | Storm tank at WwTW | SJ9300097140 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 716.37 | 70 | 23.3333 | 3 (installed 2020) | 99.99 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2149
United Utilities | TURNER LANE/ALEXANDRA ROAD | Turner Lane/Alexandra Road CSO | 016993751 | TAM0042 | SO | SO on sewer network | SJ9394098770 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | THE RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 412.86 | 123 | 110.75 | 4 (installed 2019) | 99.97 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG2150
United Utilities | LOWER WHARF STREET CSO 442EC | LOWER WHARF STREET CSO | 01TAM0043 | TAM0043 | SO | SO on sewer network | SJ9406098750 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 142.7 | 96 | 91.2 | 5 (installed 2018) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG2151
United Utilities | Lower Wharf Street/Scotland Street CSO | Lower Wharf Street/Scotland Street CSO | 016993752/2 | TAM0044 | SO | SO on sewer network | SJ9412098711 | GB112069061112 | Tame (Swineshaw Brook to Mersey) | River Tame | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 146.43 | 99 | 90.4 | 5 (installed 2018) | 89.05 | Sensor failure / issue | Resolved - Jun | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG2152
United Utilities | POTTINGER ST/OXFORD ST | Pottinger Street/Oxford Street CSO | 016993753 | TAM0045 | SO | SO on sewer network | SJ9288097810 | GB112069061152 | Medlock (Lumb Brook to Irwell) | THE RIVER TAME | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 168.78 | 84 | 74 | 4 (installed 2019) | 99.32 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG2153
United Utilities | BROADOAK/LYDHURST AVE | Broadoak/Lyndhurst Avenue CSO | 01TAM0047 | TAM0047 | SO | SO on sewer network | SD9395000310 | GB112069061151 | Medlock (Source to Lumb Brook) | TAUNTON (SMALLSHAW BECK) | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 1581.36 | 158 | 104.75 | 4 (installed 2019) | 44.73 | Comms failure / issue | Resolved - Nov | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2154
United Utilities | GREEN LANE LYNDHURST AVE CSO | Green Lane/Lyndhurst Avenue CSO | 016993675 | TAM0049 | SO | SO on sewer network | SD9376000210 | GB112069061151 | Medlock (Source to Lumb Brook) | SMALLSHAW BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.87 | 3 | 8.6 | 5 (installed 2018) | 100 | [5 empty] | UUG2155
United Utilities | GAMBREL BANK ROAD CSO 441U7 | Gambrel Bank Road CSO | 01TAM0050 | TAM0050 | SO | SO on sewer network | SD9374000740 | GB112069061151 | Medlock (Source to Lumb Brook) | DOWNSHAW BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.27 | 8 | 15.8 | 5 (installed 2018) | 100 | [5 empty] | UUG2156
United Utilities | GREENWOOD AVE PLATT AVE CSO 441XE | Greenwood Avenue/Platt Avenue CSO | 01TAM0051 | TAM0051 | SO | SO on sewer network | SD9423000520 | GB112069061151 | Medlock (Source to Lumb Brook) | SMALLSHAW BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 0.27 | 1 | 1.4 | 5 (installed 2018) | 100 | [5 empty] | UUG2157
United Utilities | NEWMARKET RD PS | Newmarket Road PS | 01TAM0054 | TAM0054 | SO | Storm discharge at pumping station | SD9250000450 | GB112069061151 | Medlock (Source to Lumb Brook) | TAUNTON BROOK, TRIB OF MEDLOCK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 78.58 | 41 | 36 | 5 (installed 2018) | 71.73 | Sensor failure / issue | Resolved - Jul | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG2158
United Utilities | ARMATHWAITE WWTW | ARMATHWAITE WwTW | 017670054 | 17670054 | SO | Inlet SO at WwTW | NY5107046370 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 85.55 | 97 | 106.5 | 6 (installed 2017) | 99.63 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 4: No cost beneficial solution | UUG2159
United Utilities | THE FLATS CSO 171U1 | The Flats CSO | 017680350 | EDE0107 | SO | SO on sewer network | NY5074046100 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2017 - full year data expected | 2 | 7 | 20.3333 | 6 (installed 2017) | 97.95 | [5 empty] | UUG2160
United Utilities | ARLECDON STW | ARLECDON WwTW | 017470024 | 17470024 | SO | Inlet SO at WwTW | NY0472019130 | GB112074070020 | Dub Beck | DUB BECK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 122.77 | 32 | 28 | 3 (installed 2020) | 100 | [5 empty] | UUG2161
United Utilities | ROWRAH PUMPING STATION | Rowrah PS | EPRBP3420GJ | COP0035 | SO | Storm discharge at pumping station | NY0611018780 | GB112075070540 | Marron | COLLIERGATE BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 406.72 | 30 | 29.4 | 5 (installed 2018) | 99.98 | [5 empty] | UUG2162
United Utilities | APPLEBY WWTW | APPLEBY WwTW(APPLE) (017670001) | 017670001 | 17670001 | ST | Storm tank at WwTW | NY6753021000 | GB102076070880 | Eden - Scandal Beck to Lyvennet | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 81.49 | 16 | 19.6 | 5 (installed 2018) | 100 | [5 empty] | UUG2163
United Utilities | HOLME ST/CHAPEL ST CSO (171ZK) | Holme Street/Chapel Street CSO | 017670168 | EDE0061 | SO | SO on sewer network | NY6815020200 | GB112073071050 | Holme Beck | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 5.1 | 11 | 10.25 | 4 (installed 2019) | 100 | [5 empty] | UUG2164
United Utilities | APPLEBY CSO | Appleby CSO Adj to Appleby WwTW | 017680301 | EDE0097 | SO | SO on sewer network | NY6766020840 | GB102076070880 | Eden - Scandal Beck to Lyvennet | RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 252.61 | 46 | 38.4 | 5 (installed 2018) | 100 |  |  | Data collection - Confirmed exceptional weather – Remaining spills not above SOAF threshold | N/A - Hydraulic capacity |  | UUG2165
United Utilities | ANTHORN PS ANTHN | Anthorn PS | 01ALL0035 | ALL0035 | SO | Storm discharge at pumping station | NY2002058380 | GB530207614700 | SOLWAY | RIVER WAMPOOL ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 60.41 | 39 | 45 | 5 (installed 2018) | 100 |  |  | Data collection - Tidal / river inundation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2166
United Utilities | AMBLESIDE WWTW | AMBLESIDE WwTW | 017370024 | 17370024 | ST | Storm tank at WwTW | NY3722003890 | GB112073071140 | Rothay | RIVER ROTHAY | N/A | Windermere, Rayrigg Meadow; Windermere, Millerground Landing | Not Applicable | Commissioned in 2018 - full year data expected | 582.03 | 46 | 66.6 | 5 (installed 2018) | 99.13 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2167
United Utilities | ALTRINCHAM STW | ALTRINCHAM WwTW | 016940141 | 16940141 | ST | Storm tank at WwTW | SJ7504090440 | GB112069060980 | Sinderland Brook | SINDERLAND BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 782.36 | 108 | 144 | 3 (installed 2020) | 99.9 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Scheduled | Other investigation - non-WINEP/Green Recovery | UUG2168
United Utilities | OAKFIELD ST COMBINED SEWER OVERFLOW | Oakfield Street CSO | 016892327 | TRA0031 | SO | SO on sewer network | SJ7744087990 | GB112069061260 | Timperley Brook | TIMPERLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 265.35 | 66 | 51.75 | 4 (installed 2019) | 76.67 | Sensor failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2169
United Utilities | STAMFORD NEW ROAD CSO | Stamford New Road CSO | 016892328 | TRA0032 | SO | SO on sewer network | SJ7739088340 | GB112069061260 | Timperley Brook | TIMPERLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 47.46 | 62 | 61.6667 | 3 (installed 2020) | 99.93 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Stage 1c: Confirmed "hydraulic issue" | UUG2170
United Utilities | BALFOUR ROAD CSO | Balfour Road CSO | 01TRA0033 | TRA0033 | SO | SO on sewer network | SJ7696089540 | GB112069061260 | Timperley Brook | TIMPERLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 1.27 | 2 | 3 | 3 (installed 2020) | 100 | [5 empty] | UUG2171
United Utilities | ALTRINHAM WWTW HIGH LEVEL OVERFLOW | Altrincham WwTW High Level Overflow (Formerly Woodcote Road CSO) | 016892363 | TRA0034 | SO | Storm discharge at pumping station | SJ7532090270 | GB112069060980 | Sinderland Brook | SINDERLAND BROOK | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 5.7 | 7 | 12.6667 | 3 (installed 2020) | 99.99 | [5 empty] | UUG2172
United Utilities | WELLINGTON ROAD CSO | Wellington Road CSO | 016940411 | TRA0072 | SO | SO on sewer network | SJ7720089290 | GB112071065270 | Darwen - conf Davy Field Bk to conf Blakewater | RIVER DARWEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 82.47 | 44 | 40.2 | 5 (installed 2018) | 56.95 | Sensor failure / issue | N/A - Ongoing investigation | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2173
United Utilities | ALSAGER STW | ALSAGER WwTW | 016810042 | 16810042 | ST | Storm tank at WwTW | SJ7891056790 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | TRIBUTARY OF RIVER DANE | N/A | N/A | Not Applicable | Commissioned in 2020 - full year data expected | 85.98 | 29 | 48.3333 | 3 (installed 2020) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2174
United Utilities | 58/64 AUDLEY ROAD CSO | 58/64 Audley Road CSO | 01CON0019 | CON0019 | SO | SO on sewer network | SJ7995054830 | GB112068074630 | Valley Brook (Source to Englesea Brook) | VALLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 29.03 | 33 | 42.4 | 5 (installed 2018) | 96.7 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2175
United Utilities | AUDLEY RD/TALKE RD JUNCTION CSO | Audley Road and Talke Road Junction CSO | EPRQB3499WS | CON0020 | SO | SO on sewer network | SJ7996755137 | GB112068074630 | Valley Brook (Source to Englesea Brook) | TRIB VALLEY BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 5.47 | 9 | 50.5 | 4 (installed 2019) | 100 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2176
United Utilities | 113 HASSALL RD CSO | HASSALL ROAD CSO | 01CON0023 | CON0023 | SO | SO on sewer network | SJ7869756899 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | DAY GREEN STREAM | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 12.4 | 19 | 20.6 | 5 (installed 2018) | 100 | [5 empty] | UUG2177
United Utilities | 29 CRESSWELLSHAWE RD B CSO 13567 | 29 Cresswellshawe Road (Overflow B) CSO | 016892426 | CON0025 | SO | SO on sewer network | SJ7989056280 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | CRESSWELLSHAWE BRK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 3.6 | 11 | 16.4 | 5 (installed 2018) | 99.41 | [5 empty] | UUG2178
United Utilities | 29 CRESSWELLSHAWE RD A CSO 13567 | 29 Cresswellshawe Road (Overflow A) CSO | 016892427 | CON0026 | SO | SO on sewer network | SJ7981156068 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | CRESSWELLSHAWE BRK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 11.8 | 44 | 99.4 | 5 (installed 2018) | 94.81 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | U_INV driver - Stage 2 or 3: Environmental / UWWTR assessments or improvement options appraisal | UUG2179
United Utilities | ASHEMORES LANE LAWTON RD CSO 131CE | Ashmores Lane/Lawton Road CSO | 016892428 | CON0027 | SO | SO on sewer network | SJ7989056281 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | CRESSWELLSHAWE BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 7.23 | 21 | 27 | 5 (installed 2018) | 99.99 | [5 empty] | UUG2180
United Utilities | HASSALL RD CREWE RD CSO 131QJ | HASSALL ROAD / CREWE ROAD CSO | 01CON0022 | CON0022 | SO | SO on sewer network | SJ7878155326 | GB112068074630 | Valley Brook (Source to Englesea Brook) | VALLEY BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.67 | 4 | 2 | 5 (installed 2018) | 99.99 | [5 empty] | UUG2181
United Utilities | LAWTON ROAD WESLEY AVE CSO 132CM | Lawton Road/Wesley Avenue CSO | 016892429 | CON0028 | SO | SO on sewer network | SJ7989056282 | GB112068055390 | Kidsgrove Stream (including Day Green Stream) | CRESSWELLSHAWE BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1.67 | 7 | 59.8 | 5 (installed 2018) | 99.99 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2182
United Utilities | MARYPORT SEWAGE PUMPING STATION | Maryport Sewage PS | 017580242 | ALL0122 | SO | Storm discharge at pumping station | NY0299036090 | 357 |  | IRISH SEA | N/A | Allonby South; Allonby West Winds | Not Applicable | Commissioned in 2017 - full year data expected | 24.78 | 11 | 31.6667 | 6 (installed 2017) | 100 | [5 empty] | UUG2183
United Utilities | JOHN PIER SEWAGE PUMPING STATION | John Pier Sewage Pumping Station CSO | 017580294 | ALL0133 | SO | Storm discharge at pumping station | NX9966029440 | 188 |  | RIVER DERWENT ESTUARY | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 31.07 | 29 | 39.25 | 4 (installed 2019) | 99.73 |  |  |  |  | Other investigation - non-WINEP/Green Recovery | UUG2184
United Utilities | ALDERLEY EDGE WWTW ALDYE | ALDERLEY EDGE WwTW | 016910001 | 16910001 | SO | Inlet SO at WwTW | SJ8283078580 | GB112069061330 | Mobberley Brook | WHITEHALL BROOK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 1423.58 | 124 | 108.6 | 5 (installed 2018) | 99.97 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Scheduled | Other investigation - non-WINEP/Green Recovery | UUG2185
United Utilities | FULSHAW CROSS CSO 271U4 | Fulshaw Cross CSO | 016982621 | MAC0157 | SO | SO on sewer network | SJ8419079580 | GB112069061330 | Mobberley Brook | WHITEHALL BROOK VIA SWS | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 39.83 | 30 | 59.2 | 5 (installed 2018) | 97.31 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2186
United Utilities | ALDERLEY EDGE WWTW CSO | Alderley Edge WwTW CSO MAC0174 | 016892364 | MAC0174 | SO | SO on sewer network | SJ8302078810 | GB112069061330 | Mobberley Brook | CARR BROOK | N/A | N/A | Not Applicable | Commissioned in 2019 - full year data expected | 708.26 | 94 | 86.5 | 4 (installed 2019) | 100 |  |  | Performance - Asset configuration (e.g. PS/rising main/storm tanks) | Scheduled | Other investigation - non-WINEP/Green Recovery | UUG2187
United Utilities | AINSTABLE WASTEWATER TREATMENT WORK | AINSTABLE WwTW | 017670046 | 17670046 | SO | Inlet SO at WwTW | NY5278046432 | GB102076073940 | Eden - Eamont to tidal | POWSY SIKE, TRIB RIVER EDEN | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 21.44 | 15 | 26.8 | 5 (installed 2018) | 99.99 | [5 empty] | UUG2188
United Utilities | AINSDALE WASTEWATER TREATMENT WORKS | AINSDALE WwTW | 016930486 | 16930486 | ST | Storm tank at WwTW | SD3203011100 | GB112069064510 | Chisnall Brook | FINE JANES BROOK | N/A | Southport | Not Applicable | Commissioned in 2017 - full year data expected | 15.15 | 4 | 20.3333 | 6 (installed 2017) | 100 | [5 empty] | UUG2189
United Utilities | OPP WEST VIEW COMBINED SEWER O/FLOW | Opp West View CSO | 01ALL0012 | ALL0012 | SO | SO on sewer network | NY1752050520 | GB102075073440 | Waver | STANK BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 17.97 | 12 | 25.6 | 5 (installed 2018) | 96.19 | [5 empty] | UUG2190
United Utilities | ABBEYTOWN PUMPING STATION | Abbeytown Pumping Station (Site ID ABETW) (ALL0104) | 017580256 | ALL0104 | SO | Storm discharge at pumping station | NY1778050600 | GB102075073440 | Waver | STANK BECK | N/A | N/A | Not Applicable | Commissioned in 2018 - full year data expected | 197.19 | 35 | 48.8 | 5 (installed 2018) | 99.23 |  |  | Not asset maintenance - Hydraulic capacity | N/A - Hydraulic capacity | Other investigation - non-WINEP/Green Recovery | UUG2191
United Utilities | TBC | Westbourne Rd CSO (512ZA) | TBC | MEOLS_UNP_504 | SO | SO on sewer network | SJ2087586694 | GB531106708200 | Dee Estuary | Dee Estuary | N/A | N/A | Not Applicable | Dec 2023 | 16.4 | 3 |  | <1 yr (installed 2023) | 97.3684 | [5 empty] | UUG2192
United Utilities | TBC | Dicketts Lane CSO (493DE) | TBC | WSTHD_UNP_501 | SO | SO on sewer network | SD 44956 07024 | GB112070064810 | Eller Brook | Eller Brook | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2193
United Utilities | TBC | Wakefield Road CSO (449LF) | TBC | DUKIN_UNP_508 | SO | SO on sewer network | SJ 97414 99922 | GB112069061110 | River Tame | River Tame | N/A | N/A | Not Applicable | Dec 2023 | 829.9 | 156 |  | <1 yr (installed 2023) | 86.3014 | Installation set-up/design issue | N/A - Ongoing investigation | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2194
United Utilities | Weston Street combined sewer overflow | Weston Street CSO (073K8) | TBC | BOL0243 | SO | SO on sewer network | SD 72462 08005 | GB112069064540 | Middle Brook | Jenny Beck Culvert via surface water sewer | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2195
United Utilities | TBC | Hypatia Street CSO (078NN) | TBC | BOLTO_UNK_503 | SO | SO on sewer network | SD 72650 09486 | GB112069064530 | Tonge | River Tonge | N/A | N/A | Not Applicable | Dec 2023 | 198.43 | 163 |  | <1 yr (installed 2023) | 97.2851 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2196
United Utilities | TBC | Manchester Road / Corrie Drive CSO (079DB) | TBC | BOL0245 | SO | SO on sewer network | SD 76377 04026 | GB112069061451 | Irwell (Croal to Irk) | Unity Brook | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2197
United Utilities | TBC | Bolton by Bowland | TBC | BOLTB_UNP_501 | SO | Inlet SO at WwTW | SD7840049300 | GB112071065570 | Skirden Beck | Skirden Beck | N/A | N/A | Not Applicable | Dec 2023 | 77.13 | 21 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2198
United Utilities | TBC | Lower Barnes Street CSO (229KM) | TBC | HYNDB_UNP_528 | SO | SO on sewer network | SD 74435 31529 | GB112071065070 | Hyndburn Brook - Lower | Hyndburn Brook | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2200
United Utilities | TBC | Longpool CSO (399KO) | TBC | KENDA_UNP_501 | SO | SO on sewer network | SD 51932 92962 | GB112073071460 | Kent - conf Sprint to tidal | River Kent | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2201
United Utilities | TBC | XXX Middleton Road CSO (131V4) | TBC | SANDB_UNK_508 | SO | SO on sewer network | SJ7494461000 | GB112068055460 | Croco | Croco | N/A | N/A | Not Applicable | Dec 2023 | 0.26 | 1 |  | <1 yr (installed 2023) | 97.2603 | [5 empty] | UUG2202
United Utilities | TBC | Highgate Jnc Lowther Street CSO (399KL) | TBC | KENDA_UNP_502 | SO | SO on sewer network | SD 51650 92639 | GB112073071460 | Kent - conf Sprint to tidal | River Kent | N/A | N/A | Not Applicable | Dec 2023 | 220.53 | 42 |  | <1 yr (installed 2023) | 74.07 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2203
United Utilities | TBC | London Road (Preston) CSO (332C8) | TBC | PREST_UNP_523 | SO | SO on sewer network | SD 55285 28748 | GB112071065470 | Savick Brook | Savick Brook | N/A | N/A | Not Applicable | Dec 2023 | 178.8 | 80 |  | <1 yr (installed 2023) | 97.2067 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2204
United Utilities | TBC | Mount Street CSO (079KM) | TBC | BOLTO_UNP_526 | SO | SO on sewer network | SD 72177 10200 | GB112069064540 | Middle Brook | River Tonge via a surface water sewer | N/A | N/A | Not Applicable | Dec 2023 | 1902 | 226 |  | <1 yr (installed 2023) | 97.9839 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2205
United Utilities | TBC | Fleming Rd CSO (263DZ) | TBC | LPOOL_UNP_505 | SO | SO on sewer network | SJ 43625 84776 | GB112069061390 | Ditton Brook (Halewood to Mersey Estuary) | Ditton Brook | N/A | N/A | Not Applicable | Dec 2023 | 1.2 | 19 |  | <1 yr (installed 2023) | 99.42 | [5 empty] | UUG2206
United Utilities | TBC | Holland Close CSO (319LC) | TBC | SDDLW_UNP_508 | SO | SO on sewer network | SD 98315 07911 | GB112069064741 | Tame (Source to Chew Brook) | River Tame | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2207
United Utilities | Hanging Green Lane combined sewer overflow (LAN0123) | Hanging Green Lane CSO (258G9) | EPR/JB3B94RC | LAN0123 | SO | SO on sewer network | SD4726266573 | GB112072065980 | Lune - conf Wenning to tidal | Hatlex Beck Via a surface water sewer | N/A | N/A | Not Applicable | Dec 2023 | 1915.1 | 120 |  | <1 yr (installed 2023) | 96.4912 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2208
United Utilities | TBC | XX North Row CSO (049KS) | TBC | BARFU_UNP_505 | SO | SO on sewer network | SD2224569445 | GB112074069790 | Mill Beck (Poaka Beck) | Mill Beck | N/A | N/A | Not Applicable | Dec 2023 | 743.93 | 71 |  | <1 yr (installed 2023) | 96.748 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2209
United Utilities | TBC | Ainsworth Road CSO (091LY) | TBC | BOLTO_UNP_511 | SO | SO on sewer network | SD 79098 07250 | GB112069060840 | Irwell (Roch to Croal) | River Irwell via surface water sewer | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2210
United Utilities | TBC | Moses Gate Country Park CSO (073I5) | TBC | BOL0242 | SO | SO on sewer network | SD 74930 06744 | GB112069064550 | Croal (including Blackshaw Brook) | River Croal | N/A | N/A | Not Applicable | Dec 2023 | 65.3 | 59 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2211
United Utilities | TBC | XXX Water Street CSO (099KN) | TBC | BOLTO_UNP_515 | SO | SO on sewer network | SD 77993 07387 | GB71210501 | Manchester, Bolton & Bury Canal | Manchester, Bolton and Bury Canal | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2212
United Utilities | TBC | Prestolee PS | TBC | BOLTO_UNP_517 | SO | Storm discharge at pumping station | SD7528305615 | GB112069061451 | Irwell (Croal to Irk) | River Irwell | N/A | N/A | Not Applicable | Dec 2023 | 30.01 | 13 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2213
United Utilities | TBC | Gamesley PS | TBC | GLOSS_UNP_501 | SO | Storm discharge at pumping station | SK0058194886 | GB112069061050 | Etherow (Glossop Brook to Goyt) | River Etherow | N/A | N/A | Not Applicable | Dec 2023 | 288.81 | 17 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2214
United Utilities | TBC | The Crescent CSO (383KE) | TBC | SOUTH_UNP_502 | SO | SO on sewer network | SD 37510 19433 | GB112070064830 | Three Pool's Waterway | Three Pool's Waterway | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2215
United Utilities | The Green combined sewer overflow (EDE0123) | O/S XXXXXX House CSO (174LB) | EPR/JB3795AR | EDE0123 | SO | SO on sewer network | NY6105327873 | GB102076070950 | Crowdundle Beck - Lower | Birk Sike | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2216
United Utilities | TBC | Delph New Road CSO (319LB) | TBC | SDDLW_UNP_509 | SO | SO on sewer network | SD9872307476 | GB112069064741 | Tame (Source to Chew Brook) | River Tame | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2217
United Utilities | TBC | Old Lancaster Lane CSO (339KV) | TBC | PREST_UNP_520 | SO | SO on sewer network | SD 52752 30240 | GB112071065470 | Savick Brook | Culverted section of Moor Brook, a tributary of the River Ribble | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2218
United Utilities | TBC | Parker Street CSO (228ES) | TBC | HYNDB_UNP_525 | SO | SO on sewer network | SD 73625 30750 | GB112071065070 | Hyndburn Brook - Lower | Hyndburn Brook via surface water sewer | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2219
United Utilities | TBC | Junction of High Street /Stockport Rd / Manchester Rd CSO | TBC | DAVYH_UNP_576 | SO | SO on sewer network | SJ8538389324 | GB112069060940 | Micker Brook | Micker Brook | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2220
United Utilities | TBC | South Strand CSO (52514) | EPRJJB3791WT | WYR0085 | SO | SO on sewer network | SD3190245466 | GB112072066250 | Wyre - conf R Brock to tidal | Culverted section of Copse Brook via a surface water sewer | N/A | N/A | Not Applicable | Dec 2023 | 195.17 | 76 |  | <1 yr (installed 2023) | 98.0769 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2221
United Utilities | TBC | Liverpool Road CSO (42062) | TBC | STHEL_UNK_501 | SO | SO on sewer network | SJ 50895 95188 | GB112069061210 | Hardshaw (Windle) Brook | Hardshaw Brook | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2222
United Utilities | TBC | Mottram Rd CSO (449BT) | TBC | DUKIN_UNP_505 | SO | SO on sewer network | SJ 96721 98549 | GB112069061110 | River Tame | River Tame | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2223
United Utilities | TBC | Cross Lane CSO (399KM) | TBC | ULVER_UNP_503 | SO | SO on sewer network | SD 30168 77537 | GB112073071160 | Dragley Beck | Dragley Beck | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2224
United Utilities | TBC | Birkby | TBC | BIRKB_UNP_501 | SO | SO on sewer network | NY0561537370 | GB112075073640 | Ellen (lower) | River Ellen | N/A | N/A | Not Applicable | Dec 2023 | 0 | 0 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2225
United Utilities | TBC | Stockport WwTW | TBC | STOCK_UNP_515 | SO | Inlet SO at WwTW | SJ 86440 89690 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | River Mersey | N/A | N/A | Not Applicable | Dec 2023 | 0 | 0 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2226
United Utilities | TBC | Moorside Road / Ellesmere Street CSO (378JX) | TBC | ECCLE_UNP_502 | SO | SO on sewer network | SD 76488 01410 | GB112069061430 | Folly Brook and Salteye Brook. | Folly Brook and Salteye Brook. | N/A | N/A | Not Applicable | Dec 2023 | 106.8 | 53 |  | <1 yr (installed 2023) | 95.5 | [5 empty] | UUG2227
United Utilities | TBC | Moorside Primary School CSO (379CM) | TBC | ECCLE_UNP_506 | SO | SO on sewer network | SD 76986 01231 | GB112069061430 | Folly Brook and Salteye Brook. | Folly Brook and Salteye Brook. | N/A | N/A | Not Applicable | Dec 2023 | 92.57 | 43 |  | <1 yr (installed 2023) | 97.28 | [5 empty] | UUG2228
United Utilities | High Road Halton combined sewer overflow (LAN0124) 259DA | High Road CSO (259DA) | EPR/JB3597EQ | LAN0124 | SO | SO on sewer network | SD5036564723 | GB112072065980 | Lune - conf Wenning to tidal | River Lune via a surface | N/A | N/A | Not Applicable | Dec 2023 | 0 | 0 |  | <1 yr (installed 2023) | 82.5328 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2229
United Utilities | TBC | Regent Road / Ordsall Lane CSO (372NO) | TBC | SALFO_UNP_504 | SO | SO on sewer network | SJ 82619 97591 | GB112069061452 | Irwell / Manchester Ship Canal (Irk to confluence with Upper Mersey) | River Irwell | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2230
United Utilities | TBC | Sagars Rd CSO (279DF) | TBC | WILML_UNP_502 | SO | SO on sewer network | SJ8522083613 | GB112069061360 | Dean (Bollington to Bollin) | Dean Brook | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2231
United Utilities | TBC | Broadway CSO Opp Football Ground (319KO) | TBC | OLD0170 | SO | SO on sewer network | SD 90451 05719 | GB112069061120 | Wince Brook | Culverted section of Wince Brook via surface water sewer | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2232
United Utilities | 9 Turton Road | 9 Turton Road | EPR/JB3890WT | BRY0138 | SO | SO on sewer network | SD7743313232 | GB112069064610 | Kirklees Brook | Unnamed tributary of Kirklees Brook | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2233
United Utilities | TBC | Liverpool Road PS (49039) | TBC | BURSC_UNP_501 | SO | Storm discharge at pumping station | SD 46172 16371 | GB112070064820 | Douglas - Lower | River Douglas | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2234
United Utilities | TBC | Pool Lane CSO (512L8) | TBC | BIRKE_UNP_507 | SO | SO on sewer network | SJ2825887685 | GB112068060530 | The Birket including Arrowe Brook and Fender | The Fender | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2235
United Utilities | TBC | Morecambe Lodge PS (25920) | TBC | CRNFT_UNP_509 | SO | Storm discharge at pumping station | SD 47245 67409 | GB112073071240 | Keer | Unnamed trib of Hatlex Beck | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2236
United Utilities | TBC | Lostock Street / Lower Vickers Street CSO (282DO) | TBC | DAVYH_UNP_574 | SO | SO on sewer network | SJ 85672 99036 | GB112069061150 | River Medlock | River Medlock | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2237
United Utilities | TBC | Great Stone Road CSO (459KP) | TBC | DAVYH_UNP_575 | SO | SO on sewer network | SJ 77842 93480 | GB112069061040 | Chorlton Brook (Princess Parkway to Mersey) | Chorlton Brook | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2238
United Utilities | TBC | Eagle Brow CSO (489KT) | TBC | WARRS_UNK_501 | SO | SO on sewer network | SJ6824987202 | GB112069061030 | Mersey (upstream of Manchester Ship Canal) | River Mersey | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2239
United Utilities | TBC | Darley Street CSO (079KL) | TBC | BOLTO_UNP_527 | SO | SO on sewer network | SD 72177 10200 | GB112069064540 | Middle Brook | River Tonge via a surface water sewer | N/A | N/A | Not Applicable | Dec 2023 | 0.47 | 2 |  | <1 yr (installed 2023) | 99.5 | [5 empty] | UUG2240
United Utilities | TBC | The Hayloft Bouth (399KN) | TBC | BOUTH_UNP_501 | SO | SO on sewer network | SD3286985685 | GB112073071420 | Leven | River Leven | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2241
United Utilities | TBC | XXXXXXXX House CSO (169KP) | TBC | CREWE_UNP_503 | SO | SO on sewer network | SJ72552 56543 | GB112073071160 | Dragley Beck | Dragley Beck | N/A | N/A | Not Applicable | Dec 2023 | 1515.1 | 97 |  | <1 yr (installed 2023) | 95.4198 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2242
United Utilities | TBC | XX Moorside Road (099KU) | TBC | BURYZ_UNP_515 | SO | SO on sewer network | SD 77511 12439 | GB112069064610 | Kirklees Brook | Kirklees Brook | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2243
United Utilities | TBC | Union Street / Whitehall Street (353CC) | TBC | ROCHD_UNP_517 | SO | SO on sewer network | SD 89762 13754 | GB112069064720 | Roch (Source to Spodden) | Culverted section of River Roch | N/A | N/A | Not Applicable | Dec 2023 | 0 | 0 |  | <1 yr (installed 2023) | 98.8889 | [5 empty] | UUG2244
United Utilities | TBC | Stainforth WwTW | TBC | STANF_UNP_501 | SO | Inlet SO at WwTW | SD3819946710 | GB112071065690 | Cowside and Stainforth Beck | Cowside and Stainforth Beck | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2246
United Utilities | TBC | Cheetham Street / St Marys Gate CSO (353CC) | TBC | ROCHD_UNP_512 | SO | SO on sewer network | SD 89762 13754 | GB112069064720 | Roch (Source to Spodden) | Culverted section of River Roch | N/A | N/A | Not Applicable | Dec 2023 |  |  |  | <1 yr (installed 2023) | 0 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2247
United Utilities | TBC | Sankey Ind Est CSO (428NI) | TBC | WARRN_UNP_516 | SO | SO on sewer network | SJ 57205 94497 | GB112069061200 | Sankey Brook (Rainford Brook to Mersey) | Sankey Brook | N/A | N/A | Not Applicable | Dec 2023 | 0.26 | 2 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2248
United Utilities | ACTON BRIDGE STW | Acton Bridge WwTW | 16810039 | ACTON_UNP_502 | SO | Inlet SO at WwTW | NY5077055350 | GB102076073900 | Trout Beck (Cairn Beck) | TRIB TROUT BECK | N/A | N/A | Not Applicable | Dec 2023 | 112.97 | 30 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2249
United Utilities | AINSDALE WASTEWATER TREATMENT WORKS | Ainsdale WwTW | 16930486 | AINSD_UNP_504 | ST | Storm tank at WwTW | SD3203011100 | GB112069064510 | Chisnall Brook | Fine Janes Brook | N/A | N/A | Not Applicable | Dec 2023 | 43.07 | 15 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2250
United Utilities | TBC | Cocklakes WwTW | TBC | COCKL_UNP_501 | SO | Inlet SO at WwTW | NY4620051100 | GB102076073910 | Pow Maughan Beck | TRIB POW MAUGHAN BECK | N/A | N/A | Not Applicable | Dec 2023 | 79.03 | 38 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2251
United Utilities | TBC | Faugh WwTW | TBC | FAUGH_UNP_501 | SO | Inlet SO at WwTW | NY5077055350 | GB102076073900 | Trout Beck (Cairn Beck) | TRIB TROUT BECK | N/A | N/A | Not Applicable | Dec 2023 | 14.53 | 8 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2252
United Utilities | GREAT CLIFTON STW | Great Clifton | 17570042 | GRCLI_UNP_501 | SO | Inlet SO at WwTW | NY0329029860 | GB112075070520 | Derwent - conf Cocker to tidal | RIVER DERWENT | N/A | N/A | Not Applicable | Dec 2023 | 440.33 | 55 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2253
United Utilities | HETHERSGILL STW | Hethers Gill WwTW | 17770001 | HETHE_UNP_501 | SO | Inlet SO at WwTW | NY4606066540 | GB102077074150 | Hether Burn | HETHER BURN | N/A | N/A | Not Applicable | Dec 2023 | 406.17 | 59 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2254
United Utilities | HIGH NEWTON STW | High Newton WwTW | 17370047 | HIGHN_UNP_501 | SO | Inlet SO at WwTW | SD3988082900 | GB112073071270 | Eea | TRIB AYSIDE POOL | N/A | N/A | Not Applicable | Dec 2023 | 900.63 | 80 |  | <1 yr (installed 2023) | 100 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2255
United Utilities | HOLDEN STW | Holden WwTW | 17160038 | HOLDE_UNP_501 | SO | Inlet SO at WwTW | SD7775049150 | GB112071065550 | Holden Beck | HOLDEN BECK | N/A | N/A | Not Applicable | Dec 2023 | 4.6 | 6 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2256
United Utilities | HOO GREEN STW | Hoo Green WwTW | 16810082 | HOOGE_UNP_501 | SO | Inlet SO at WwTW | SJ7188082520 | GB112068060410 | Smoker Brook (Gale Brook to Wincham Brook) | TABLEY BROOK | N/A | N/A | Not Applicable | Dec 2023 | 0 | 0 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2257
United Utilities | IREBY WWTW | Ireby WwTW | 17570071 | IRBYZ_UNP_501 | SO | Inlet SO at WwTW | NY2405039260 | GB112075073630 | Ellen (upper) | River Ellen | N/A | N/A | Not Applicable | Dec 2023 | 406.03 | 62 |  | <1 yr (installed 2023) | 100 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2258
United Utilities | KERSHOPEFOOT VILLAGE STW | Kershopefoot WwTW | 17790013 | KERSH_INP_501 | SO | Inlet SO at WwTW | NY4850083500 | GB102077074190 | Esk (Eden and Esk) | KERSHOPE BURN | N/A | N/A | Not Applicable | Dec 2023 | 1816.07 | 85 |  | <1 yr (installed 2023) | 100 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2259
United Utilities | LANE BOTTOM STW | Lanebottom WwTW | 17160059 | LANEB_UNP_501 | SO | Inlet SO at WwTW | SD8760035800 | GB112071065130 | Walverden Water | PIG HOLE CLOUGH | N/A | N/A | Not Applicable | Dec 2023 | 85.87 | 26 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2260
United Utilities | LONG MARTON WEST STW | Long Marton WwTW | 17670016 | LONGM_UNP_501 | SO | Inlet SO at WwTW | NY6638024200 | GB102076070930 | Trout Beck | TROUT BECK | N/A | N/A | Not Applicable | Dec 2023 | 0.9 | 4 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2261
United Utilities | OULTON STW | Oulton WwTW | 17570015 | OULTO_UNP_501 | SO | Inlet SO at WwTW | NY2396050520 | GB102075073440 | Waver | COLMIRE SOUGH | N/A | N/A | Not Applicable | Dec 2023 | 27.8 | 14 |  | <1 yr (installed 2023) | 75.4902 | Installation set-up/design issue | N/A - Ongoing investigation |  |  |  | UUG2262
United Utilities | PILLING WASTEWATER TREATMENT WORKS | Pilling WwTW | 17260137 | PILLI_UNP_501 | SO | Inlet SO at WwTW | SD4077048960 | GB112072065860 | Pilling Water | BROAD FLEET | N/A | N/A | Not Applicable | Dec 2023 | 0 | 0 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2263
United Utilities | TBC | Sproston WWTW | TBC | SPROS_UNP_501 | SO | Inlet SO at WwTW | SJ7325066580 | GB112068055460 | Croco | RIVER CROCO | N/A | N/A | Not Applicable | Dec 2023 | 5.73 | 8 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2264
United Utilities | TABLEY STW | Tabley WWTW | 16810109 | TABLE_UNP_501 | SO | Inlet SO at WwTW | SJ7194079500 | GB112068060410 | Smoker Brook (Gale Brook to Wincham Brook) | TABLEY BROOK | N/A | N/A | Not Applicable | Dec 2023 | 85.67 | 25 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2265
United Utilities | WARWICK BRIDGE STW | Warwick Bridge WWTW | 17670074 | WARWI_UNP_501 | SO | Inlet SO at WwTW | NY4722057670 | GB102076073940 | Eden - Eamont to tidal | RIVER EDEN | N/A | N/A | Not Applicable | Dec 2023 | 0 | 0 |  | <1 yr (installed 2023) | 100 | [5 empty] | UUG2266
United Utilities | TBC | Wetheral Pastures WwTW | TBC | WETHP_UNP_501 | SO | Inlet SO at WwTW | NY4552053400 | GB102076073910 | Pow Maughan Beck | POW MAUGHAN BECK | N/A | N/A | Not Applicable | Dec 2023 | 647.5 | 100 |  | <1 yr (installed 2023) | 100 |  |  | N/A - Ongoing investigation | N/A - Ongoing investigation | Other investigation - non-WINEP/Green Recovery | UUG2267